## Slide 1: VELO Discussion
Stuart Lunt

## Slide 2: Chiller manufacturing
Planning 12-15 weeks for manufacturing
Aim for delivery in October
Planned the next two weeks for communication with companies and procurement discussion.

## Slide 3: CO2 start up
No stepper for CO2 – start-up is managed with logic
Pump has a subcooling limit that must be reached before it can run
Controllers depend on pump run status or PCO run status

## Slide 4: Accumulator Automatic set point
Sets the minimum allowable temperature to draw CO2 from the transfer lines
(*Default value*)
AC4054_Asp := AC4054_Usp
(*Emptying*)
IF P1.RunOSt AND LB1 Manifold emptying THEN
AC4054_Asp := MinAllowT

## Slide 5: Accumulator Temperature set point
Maintains safe set point value
(*Default value*)
AC4054_Tsp := MAX(AC4054_Usp, AC4054_Asp)
(*Setpoint limits*)
IF AC4054_Tsp >= AC4054_Tsp_tH THEN
AC4054_Tsp := AC4054_Tsp_tH
ELSE IF AC4054_Tsp <= AC4054_Tsp_tL THEN
AC4054_Tsp = AC4054_Tsp_tL
END IF

## Slide 6: Local box
Logically EV1a08 and EV9a60 are considered as part of the local box.
There are BDs near the transfer line but it may be possible to manually trap CO2

## Slide 7: Safety volume in LB
If a failure occurs the experiment valves will close when the PCO returns to the safe position
It may be better to add a safety valve or volume to the local box

## Slide 8: Local box stepper
The system is in bypass configuration in the safe position
The CO2 PCO and the Local box PCO can operate independently

## Slide 9: Operation stepper

## Slide 10: Connecting stepper

## Slide 11: Disconnecting branch

## Slide 12: Three-way valve control
A word parameter will be used to set the position of the valve
Logic will make sure only one is opened at a time.
In UNICOS it will be controlled by three OnOff valve objects which each control one of the output positions

## Slide 13: Leak test
Local box has a calculated variable M1_Leak which calculates PT/TT so it can be monitored by the user.
The user indicates when they are satisfied with it

## Slide 14: Chiller low load detection + Turbo mode
Turbo mode was not used in the MAUVE chiller
I have not included it in the FA as a result
Will it be more useful with the new refrigerant?
Do you know which refrigerant is likely to be used?

## Slide 15: Interlocks
CS0c_P1_TT_IOEr_AL | left temperature sensor wire break
CS0c_P1_PT_IOEr_AL | Left pressure sensor wire break
CS0c_P1_LP1a02_CB_TS | LP1a02 circuit breaker tripped
CS0c_P1_LP1a02_mP_FS | LP1a02 membrane pressure too high
CS0c_P1_12QA2_TS | P1 heater circuit breaker tripped
CS0c_P1_EH2a02_ACB_TS | Any heater circuit breaker tripped
CS0c_P1_EH1a04_ACB_TS | Any heater circuit breaker tripped
CS0c_P1_EH1a24_ACB_TS | Any heater circuit breaker tripped
CS0c_P1_EH4a54_ACB_TS | Any heater circuit breaker tripped
CS0c_P1_EH2a02_TS_FS | EH2a02 thermal switch tripped
CS0c_P1_EH1a04_TS_FS | EH1a04 thermal switch tripped
CS0c_P1_EH1a24_TS_FS | EH1a24 thermal switch tripped
CS0c_P1_EH4a54_TS_FS | EH4a54 thermal switch tripped
CS0c_P1_EH2a02_ATS_FS | Any heater thermal switch tripped
CS0c_P1_EH1a04_ATS_FS | Any heater thermal switch tripped
CS0c_P1_EH1a24_ATS_FS | Any heater thermal switch tripped
CS0c_P1_EH4a54_ATS_FS | Any heater thermal switch tripped
CS0c_P1_EH2a02_OT_FS | Any heater over temperature
CS0c_P1_EH1a04_OT_FS | Any heater over temperature
CS0c_P1_EH1a24_OT_FS | Any heater over temperature
CS0c_P1_EH4a54_OT_FS | Any heater over temperature
CS0c_P1_EH_A_ON_TS | EH_A power supply off
CS0c_P2_TT_IOEr_AL | Right temperature sensor wire break
CS0c_P2_PT_IOEr_AL | Right pressure sensor wire break
CS0c_P2_LP1b02_CB_TS | LP1b02 circuit breaker tripped
CS0c_P2_LP1b02_mP_FS | LP1b02 membrane pressure too high
CS0c_P2_13QA2_TS | P2 heater circuit breaker tripped
CS0c_P2_EH2b02_ACB_TS | Any heater circuit breaker tripped
CS0c_P2_EH1b04_ACB_TS | Any heater circuit breaker tripped
CS0c_P2_EH1b24_ACB_TS | Any heater circuit breaker tripped
CS0c_P2_EH4b54_ACB_TS | Any heater circuit breaker tripped
CS0c_P2_EH2b02_TS_FS | EH2b02 thermal switch tripped
CS0c_P2_EH1b04_TS_FS | EH1b04 thermal switch tripped
CS0c_P2_EH1b24_TS_FS | EH1b24 thermal switch tripped
CS0c_P2_EH4b54_TS_FS | EH4b54 thermal switch tripped
CS0c_P2_EH2b02_ATS_FS | Any heater thermal switch tripped
CS0c_P2_EH1b04_ATS_FS | Any heater thermal switch tripped
CS0c_P2_EH1b24_ATS_FS | Any heater thermal switch tripped
CS0c_P2_EH4b54_ATS_FS | Any heater thermal switch tripped
CS0c_P2_EH2b02_OT_FS | Any heater over temperature
CS0c_P2_EH1b04_OT_FS | Any heater over temperature
CS0c_P2_EH1b24_OT_FS | Any heater over temperature
CS0c_P2_EH4b54_OT_FS | Any heater over temperature
CS0c_P2_EH_B_ON_TS | EH_B power supply off
CS0c_C0_CV5e12_CEr_TS | CV5e12 carel driver error
CS0c_C0_CV5f14_CEr_TS | CV5f14 carel driver error
CS0c_Plant_FS | Plant error
CS0c_Plant_W | Plant warning
CS0c_Pump_FS | Pump error
CS0c_Pump_W | Pump warning
CS0c_C1_FS | Chiller error
CS0c_C1_W | Chiller warning
CS0c_EH_W | Heater warning
CS0c_Pres_W | Pressure warning
CS0c_Valve_FS | Valve error
CS0c_Valve_W | Valve warning
CS0c_Temp_FS | Temperature error
CS0c_Temp_W | Temperature warning
CS0c_Flow_W | Flow warning
CS0c_P0_24VDC_PS_FS | 24V DC error
CS0c_P0_24VAC_PS_FS | 
CS0c_C0_ChTT_IOEr_AL | Any chiller temperature sensor wire break
CS0c_C0_ChPT_IOEr_AL | Any chiller pressure sensor wire break
CS0c_C0_PS5020_HP_FS | High pressure alarm from PS5020
CS0c_C0_PS5020_LP_FS | Low pressure alarm from PS5020
CS0c_C0_GP5020_CB_FS | Compressor circuit breaker tripped
CS0c_C0_HX5002_CB_TS | Condenser fan circubt breaker tripped
CS0c_P0_24VDC_CB_FS | 24VDC circuit breaker trip
CS0c_P0_24VAC_CB_FS | 24VAC transformer circuit breaker trip
CS0c_P0_Misc_CB_FS | Cabinet equipment circuit breaker trip

## Slide 16: Interlocks
CS0c_P1_Ptmax_AL | Any pressure A high
CS0c_P1_LP1a02_DP_AL | Differential pressure over LP1a02
CS0c_P1_LP1a02_HP_FS | LP1a02 discharge pressure too high
CS0c_P1_LP1a02_SC_AL | LP1a02 subcoolong too low
CS0c_P1_LP1a02_nFL_FS | LP1a02 no flow full stop
CS0c_P1_EH2a02_HT_TS | EH2a02 temperature high
CS0c_P1_EH1a04_HT_TS | EH1a04 temperature high
CS0c_P1_EH1a24_HT_TS | EH1a24 temperautre high
CS0c_P1_EH4a54_HT_TS | EH4a54 temperature high
CS0c_P1_EH4a54_HP_TS | EH4a54 interlocked due to AC4a54 high pressure
CS0c_P2_Ptmax_AL | Any pressure B high
CS0c_P2_LP1b02_DP_AL | Differential pressure over LP1b02
CS0c_P2_LP1b02_HP_FS | LP1b02 discharge pressure too high
CS0c_P2_LP1b02_SC_AL | LP1b02 subcoolong too low
CS0c_P2_LP1b02_nFL_FS | LP1b02 no flow full stop
CS0c_P2_EH2b02_HT_TS | EH2b02 temperature high
CS0c_P2_EH1b04_HT_TS | EH1b04 temperature high
CS0c_P2_EH1b24_HT_TS | EH1b24 temperautre high
CS0c_P2_EH4b54_HT_TS | EH4b54 temperature high
CS0c_P2_EH4b54_HP_TS | EH4b54 interlocked due to AC4b54 high pressure
CS0c_C0_GP5020_HP_FS | GP5020 discharge pressure high
CS0c_C0_GP5020_LP_FS | GP5020 suction pressure too low
CS0c_C0_SH5018_FS | Suction superheating too low
CS0c_C0_TT5018_FS | Suction temperature
CS0c_P1_TT9a68_TS | CO2 A temperature too low
CS0c_P2_TT9b68_TS | CO2 B temperature too low
CS0c_C0_TT5004_AL | Condensation temperature too high
CS0c_C0_ST5a10_TS | A accumulator evaporation temperature low
CS0c_C0_ST5b10_TS | A condensor evaporation temperature low
CS0c_C0_ST5c10_TS | B accumulator evaporation temperature low
CS0c_C0_ST5d10_TS | B condensor evaporation temperature low
CS0c_C0_GP5020_HT_FS | Discharge temperature high
CS0c_C0_SC5004_AL | Subcooling low after the condensor
CS0c_C0_GP5020_ONF_FS | Chiller start stop limit exceeded

## Slide 17: Alarm groups – Common

## Slide 18: Alarm groups

## Slide 19: Alarm groups