## IO
Type | Card | Channel Number | Old | New | Comments | Column1 | Total IO:
DI | B1 | 0.0 | TL-VL102 open | GH9a60 | Position indicator | 1(24),2(di) | DI | 112 | xd1 | 1 | 2
DI | B1 | 0.1 | TL-VL102 close | GL9a60 | Position indicator |  | DO | 96 |  | 3 | 4
DI | B1 | 0.2 | TL-VL102move | EV9a60_RUN | In motion |  | AI | 80 |  | 5 | 6
DI | B1 | 0.3 | TL-VL103 prt 2 | GH1a08 | Connect EV1a08 here because it is three way |  | AO | 16 |  | 7 | 8
DI | B1 | 0.4 | TL-VL103 close | GM1a08 | [5 empty] | 9 | 10
DI | B1 | 0.5 | TL-VL103 prt 3 | GL1a08 | [5 empty] | 11 | 12
DI | B1 | 0.6 | TL-VL103move | EV1a08_RUN | [5 empty] | 13 | 14
DI | B1 | 0.7 | TL-VL104 open | GH4a54 | [5 empty] | 15 | 16
DI | B1 | 1.0 | TL-VL104close | GL4a54 | [5 empty] | 17 | 18
DI | B1 | 1.1 | TL-VL104 move | EV4a54_RUN | [5 empty] | 17 | 18
DI | B1 | 1.2 | TL-VL109 open | GH1a21 | [5 empty] | 1 | 1
DI | B1 | 1.3 | TL-VL109 close | GL1a21 | [5 empty] | 21 | 22
DI | B1 | 1.4 | TL-VL109 move | EV1a21_RUN | [5 empty] | 23 | 24
DI | B1 | 1.5 | TL-VL111open | GH4b54 | Connected to TL_VL103 |  |  |  |  | 25 | 26
DI | B1 | 1.6 | TL-VL111 close | GL4b54
DI | B1 | 1.7 | TL-VL111 move | EV4b54_RUN
DI | B1 | 2.0 | TL-VL112 open | GH1b21
DI | B1 | 2.1 | TL-VL112 close | GL1b21
DI | B1 | 2.2 | TL-VL112 move | EV1b21_RUN
DI | B1 | 2.3 | TR-VL102open | GH9b60
DI | B1 | 2.4 | TR-VL102 close | GL9b60
DI | B1 | 2.5 | TR-VL102 move | EV9b60_RUN
DI | B1 | 2.6 | TR-VL103 prt 2 | GH1b08
DI | B1 | 2.7 | TR-VL103 close | GM1b08
DI | B1 | 3.0 | TR-VL103 prt 3 | GL1b08
DI | B1 | 3.1 | TR-VL103 move | EV1b08_RUN
DI | B1 | 3.2 | TR-VL104open
DI | B1 | 3.3 | TR-VL104 close
DI | B1 | 3.4 | TR-VL104 move
DI | B1 | 3.5 | TR-VL108 prt 2
DI | B1 | 3.6 | TR-VL108 close
DI | B1 | 3.7 | TR-VL108 prt 3
DI | B2 | 4.0 | TR-VL108move | TSA_OK
DI | B2 | 4.1 | TR-VL109 open | TSB_OK
DI | B2 | 4.2 | TR-VL109close | LP1a02_TS
DI | B2 | 4.3 | TR-VL109 move | LP1b02_TS
DI | B2 | 4.4 | TR-VL111 open | GP5020_TS
DI | B2 | 4.5 | TR-VL111 close | PS1a02
DI | B2 | 4.6 | TR-VL111 move | PS1b02
DI | B2 | 4.7 | TR-VL112 open | EMS_OK
DI | B2 | 5.0 | TR-VL112 close | 3P_Volt_OK
DI | B2 | 5.1 | TR-VL112move
DI | B2 | 5.2 | TLR-VL101 prt 2
DI | B2 | 5.3 | TLR-VL101 close
DI | B2 | 5.4 | TLR-VL101 prt 3
DI | B2 | 5.5 | TLR-VL101 move
DI | B2 | 5.6 | TLR-VL109 prt 2
DI | B2 | 5.7 | TLR-VL109 close
DI | B2 | 6.0 | TLR-VL109 prt 3
DI | B2 | 6.1 | TLR-VL109 move
DI | B2 | 6.2 | TLR-VL110 open
DI | B2 | 6.3 | TLR-VL110 close
DI | B2 | 64 | TLR-VL110 move
DI | B2 | 6.5 | TLR-VL111 open
DI | B2 | 6.6 | TLR-VL111close
DI | B2 | 6.7 | TLR-VL111 move
DI | B2 | 7.0 | ESD205
DI | B2 | 7.1 | ESD205
DI | B2 | 7.2 | EXD1311
DI | B2 | 7.3 | EXD1311
DI | B2 | 7.4 | EXD1306
DI | B2 | 7.5 | EXD1306
DI | B2 | 7.6
DI | B2 | 7.7
DI | B3 | 8.0 | TL-PM101 on | GP5020_CB_OK
DI | B3 | 8.1 | TL-PT103 mem | HX5002_CB_OK
DI | B3 | 8.2 | TR-PM101 on | LT_CB_OK
DI | B3 | 8.3 | TR-PT103 mem | 24VDC_CB_OK
DI | B3 | 8.4 | TLR-PM101 on | LP1a02_CB_OK
DI | B3 | 8.5 | TLR-PT103 mem | LP1b02_CB_OK
DI | B3 | 8.6 | SA-PM101 Status | 24VAC_CB_OK
DI | B3 | 8.7 | SA-PT108 L | EHA_CB_OK
DI | B3 | 9.0 | SA-PT108 H | EHB_CB_OK
DI | B3 | 9.1 | SB-PM101 on | Cab_CB_OK | cabinet fan
DI | B3 | 9.2 | SB-PT108 L | Phase_CB_OK
DI | B3 | 9.3 | SB-PT108 H | CO2A_DC_CB_OK
DI | B3 | 9.4 | Clixon status | CO2B_DC_CB_OK | Heater thermal switches
DI | B3 | 9.5 | Th C1 status | Sensor_DC_CB_OK | Left thermal circuit breaker
DI | B3 | 9.6 | Th C2 status | EMS_DC_CB_OK | Backup thermal circuit breaker
DI | B3 | 9.7 | Th C3 status | Cabinet_DC_CB_OK | Right thermal circuit breaker
DI | B3 | 10.0 | SB Pm101 th rel. | EHA_ON_DI
DI | B3 | 10.1 | SA Motor Protec | EHB_ON_DI
DI | B3 | 10.2 | Rack C02 leak | LP1a02_ON_DI | Floats in bottom of tray?
DI | B3 | 10.3 | Rack A-B leak | LP1b02_ON_DI | Floats in bottom of tray?
DI | B3 | 10.4 | Heater status | GP5020_ON_DI
DI | B3 | 10.5 | I10.5Vac.Stat. | HX5002_ON_DI
DI | B3 | 10.6 | I 10.6 Vac. Stat. | 24VDC_OK
DI | B3 | 10.7 | I 10.7 Vac. Stat | PS5020_L
DI | B3 | 11.0 | Alow A | PS5020_OK | ?
DI | B3 | 11.1 | Alow C | PS5020_H | ?
DI | B3 | 11.2 | Smoke | CV5e12_OK | ?
DI | B3 | 11.3 | Chilled | CV5f14_OK
DI | B3 | 11.4 | UPSbatt
DI | B3 | 11.5 | UPS main
DI | B3 | 11.6
DI | B3 | 11.7
DO | B4 | 0.0 | TL-VL102 open | EV9a60_ODO
DO | B4 | 0.1 | TL-VL102 close | EV9a60_CDO
DO | B4 | 0.2 | TL-VL103 prt 2 | EV1a08_PRT1_DO
DO | B4 | 0.3 | TL-VL103 close | EV1a08_CDO
DO | B4 | 0.4 | TL-VL103 prt 3 | EV1a08_PRT2_DO
DO | B4 | 0.5 | TL-VL104 open | EV4a54_ODO
DO | B4 | 0.6 | TL-VL104 close | EV4a54_CDO
DO | B4 | 0.7 | TL-VL109 open | EV1a21_ODO
DO | B4 | 1.0 | TL-VL109 close | EV1a21_CDO
DO | B4 | 1.1 | TL-VL111 open | EV1b21_ODO
DO | B4 | 1.2 | TL-VL111 close | EV1b21_CDO
DO | B4 | 1.3 | TL-VL112 open | EV4b54_ODO
DO | B4 | 1.4 | TL-VL112 close | EV4b54_CDO
DO | B4 | 1.5 | TR-VL102 open | EV9b60_ODO
DO | B4 | 1.6 | TR-VL102 close | EV9b60_CDO
DO | B4 | 1.7 | TR-VL103 prt 2 | EV1b08_PRT1_DO
DO | B4 | 2.0 | TR-VL103 close | EV1b08_CDO
DO | B4 | 2.1 | TR-VL103 prt 3 | EV1b08_PRT2_DO
DO | B4 | 2.2 | TR-VL104 open | EH1a02_DO
DO | B4 | 2.3 | TR-VL104 close | EH1a04_DO
DO | B4 | 2.4 | TR-VL108 prt 2 | EH1a24_DO
DO | B4 | 2.5 | TR-VL108 close | EH4a54_DO
DO | B4 | 2.6 | TR-VL108 prt 3 | EH1b02_DO
DO | B4 | 2.7 | TR-VL109 open | EH1b04_DO
DO | B4 | 3.0 | TR-VL109 close | EH1b24_DO
DO | B4 | 3.1 | TR-VL111 open | EH4b54_DO
DO | B4 | 3.2 | TR-VL111 close | LP1a02_DO
DO | B4 | 3.3 | TR-VL112 open | LP1b02_DO
DO | B4 | 3.4 | TR-VL112 close | GP5020_DO
DO | B4 | 3.5 | Q 3.5 | HX5002_DO
DO | B4 | 3.6 | Q 3.6 | EHA_DO
DO | B4 | 3.7 | Q 3.7 | EHB_DO
DO | B5 | 4.0 | TLR-VL101 prt 2
DO | B5 | 4.1 | TLR-VL101 close
DO | B5 | 4.2 | TLR-VL101 prt 3
DO | B5 | 4.3 | TLR-VL109 prt 2
DO | B5 | 4.4 | TLR-VL109 close
DO | B5 | 4.5 | TLR-VL109 prt 3
DO | B5 | 4.6 | TLR-VL110 open
DO | B5 | 4.7 | TLR-VL110 close
DO | B5 | 5.0 | TLR-VL111 open
DO | B5 | 5.1 | TLR-VL111 close
DO | B5 | 5.2 | Q 5.2 Ready A |  | ?
DO | B5 | 5.3 | Q 5.3 Ready C |  | ?
DO | B5 | 5.4 | Q 5.4 Vent Inhib. |  | Signal from vacuum cabinet
DO | B5 | 5.5 | Q 5.5
DO | B5 | 5.6 | Q 5.6
DO | B5 | 5.7 | Q 5.7
DO | B5 | 6.0 | TL-PM101 on
DO | B5 | 6.1 | TR-PM101 on
DO | B5 | 6.2 | TLR-PM101 on
DO | B5 | 6.3 | SB1-PM101on
DO | B5 | 64 | SB2-Fan on
DO | B5 | 6.5 | Heater Power Off
DO | B5 | 6.6 | Q 6.6
DO | B5 | 6.7 | Q 6.7
DO | B5 | 7.0 | Q7.0Br.HTR1 |  | Bridge heater 1
DO | B5 | 7.1 | Q 7.1 Br. HTR2 |  | Bridge heater 2
DO | B5 | 7.2 | Q 7.2
DO | B5 | 7.3 | Q 7.3
DO | B5 | 7.4 | Q 7.4
DO | B5 | 7.5 | Q 7.5
DO | B5 | 7.6 | Q 7.6
DO | B5 | 7.7 | Q 7.7
DO | B6 | 8.0 | TL-HT101 | CO2A_DC_CB_DO
DO | B6 | 8.1 | TL-HT102 | CO2B_DC_CB_DO
DO | B6 | 8.2 | TL-HT103 | Sensor_DC_CB_DO
DO | B6 | 8.3 | TL-HT104 | EMS_DC_CB_DO
DO | B6 | 8.4 | TL-HT105 | Cabinet_DC_CB_DO
DO | B6 | 8.5 | TR-HT101 | EX5a08_DO | Cabinet SSRs
DO | B6 | 8.6 | TR-HT102 | EX5b08_DO | Cabinet SSRs
DO | B6 | 8.7 | TR-HT103 | EX5c08_DO | Cabinet SSRs
DO | B6 | 9.0 | TR-HT104 | EX5d08_DO | Cabinet SSRs
DO | B6 | 9.1 | TR-HT105
DO | B6 | 9.2 | TLR-HT102
DO | B6 | 9.3 | Q 9.3
DO | B6 | 9.4 | Q 9.4
DO | B6 | 9.5 | Q 9.5
DO | B6 | 9.6 | Q 9.6
DO | B6 | 9.7 | Q 9.7
DO | B6 | 10.0 | SA-VL106
DO | B6 | 10.1 | SA-VL110
DO | B6 | 10.2 | SA-VL114
DO | B6 | 10.3 | SA-VL119
DO | B6 | 10.4 | SB-VL106 |  | Expansion valves
DO | B6 | 10.5 | SB-VL110 |  | Expansion valves
DO | B6 | 10.6 | SB-VL114 |  | Expansion valves
DO | B6 | 10.7 | SB-VL119 |  | Expansion valves
DO | B6 | 11.0 | Q 11.0
DO | B6 | 11.1 | Q 11.1
DO | B6 | 11.2 | Q 11.2
DO | B6 | 11.3 | Q 11.3
DO | B6 | 11.4 | Q 11.4
DO | B6 | 11.5 | Q 11.5
DO | B6 | 11.6 | Q 11.6
DO | B6 | 11.7 | Q 11.7
AI | B7 | 1 | Curr.TL_HT01 (NOT CONNECTED) | PT1A04
AI | B7 | 2 | Curr.TL_HT02 | PT1A16
AI | B7 | 3 | Curr.TL_HT03 | PT9A52
AI | B7 | 4 | Curr.TL_HT04 | PT9A66
AI | B7 | 5 | Curr.TR_HT01 (NOT CONNECTED) | PT4A54
AI | B7 | 6 | Curr.TR_HT02 | PT1B04
AI | B7 | 7 | Curr.TR_HT03 | PT1B16
AI | B7 | 8 | Curr.TR_HT04 | PT9B52
AI | B7 | 9 | TL_PT001 | PT9B66 | Control (distribution) box pressure sensors
AI | B7 | 10 | TL_PT002 | PT4B54 | Control (distribution) box pressure sensors
AI | B7 | 11 | TL_PT003 | PT5004 | Control (distribution) box pressure sensors
AI | B7 | 12 | TR_PT001 | PT5A10 | Control (distribution) box pressure sensors
AI | B7 | 13 | TR_PT002 | PT5b10 | Control (distribution) box pressure sensors
AI | B7 | 14 | TR_PT003 | PT5c10 | Control (distribution) box pressure sensors
AI | B7 | 15 | TL_PT101 | PT5d10
AI | B7 | 16 | TL_PT102 | PT5018
AI | B8 | 1 | TL_PT104 | LT4a54
AI | B8 | 2 | TR_PT101 | LT4b54
AI | B8 | 3 | TR_PT102 | TT2a02
AI | B8 | 4 | TR_PT104 | TT1a04
AI | B8 | 5 | SA_PT101 | TT1a24
AI | B8 | 6 | SA_PT102 | TT4a54
AI | B8 | 7 | SA_PT103 | TT2b02
AI | B8 | 8 | SA_PT104 | TT1b04
AI | B8 | 9 | SA_PT105 | TT1b24
AI | B8 | 10 | SA_PT106 | TT4b54
AI | B8 | 11 | SA_PT107 | TT1a02
AI | B8 | 12 | SB_PT102 | TT1a10
AI | B8 | 13 | SB_PT103 | TT1a16
AI | B8 | 14 | SB_PT104 | TT9a52
AI | B8 | 15 | SB_PT105 | TT9a56
AI | B8 | 16 | SB_PT106
AI | B9 | 1 | Temp Rack | PT9a66
AI | B9 | 2 | Temp Rack | PT9b66
AI | B9 | 3 | TL_TT121
AI | B9 | 4 | TL_TT122 | TT1a02a | TC
AI | B9 | 5 | TL_TT123 | TT1a04 | TC
AI | B9 | 6 | TL_TT124 | TT1a24 | TC
AI | B9 | 7 | TL_TT125 | TT4a54 | TC
AI | B9 | 8 | TR_TT121
AI | B9 | 9 | TR_TT122 | TT1b02a | TC
AI | B9 | 10 | TR_TT123 | TT1b04 | TC
AI | B9 | 11 | TR_TT124 | TT1b24 | TC
AI | B9 | 12 | TR_TT125 | TT4b54 | TC
AI | B9 | 13 | TLR_TT122
AI | B9 | 14 | PIW 730 |  | Don't know what this is
AI | B9 | 15 | TL_LT101 | TT5c16 | PT100
AI | B9 | 16 | TR_LT101 | TT5c16
AI | B10 | 1 | SA_TT109 | TT5002 | PT100s use 2 channels in 4 wire mode
AI | B10 | 2 | SA_TT113 | TT5002
AI | B10 | 3 | SA_TT116 | TT5004
AI | B10 | 4 | SA_TT118 | TT5004
AI | B10 | 5 | PA_TT102 | TT5006
AI | B10 | 6 | PB_TT101 | TT5006
AI | B10 | 7 | PB_TT102 | TT5a10
AI | B10 | 8 | SB_TT115 | TT5a10
AI | B10 | 9 | SB_TT116 | TT5b10
AI | B10 | 10 | SB_TT117 | TT5b10
AI | B10 | 11 | SB_TT118 | TT5c10
AI | B10 | 12 | SB_TT119 | TT5c10
AI | B10 | 13 | SB_TT020 | TT5d10
AI | B10 | 14 | PT100 Haptas | TT5d10
AI | B10 | 15 | PT100 Haptas | TT5018
AI | B10 | 16 | PT100 Haptas | TT5018
DI | B11 | 1
DI | B11 | 2
DI | B11 | 3
DI | B11 | 4
DI | B11 | 5
DI | B11 | 6
DI | B11 | 7
DI | B11 | 8
AO | B11 | 1 |  | CV5e12_AO
AO | B11 | 2 |  | CV5f14_AO
AO | B11 | 3
AO | B11 | 4
AO | B11 | 5
AO | B11 | 6
AO | B11 | 7
AO | B11 | 8
AO | B11 | 9
AO | B11 | 10
AO | B11 | 11
AO | B11 | 12
AO | B11 | 13
AO | B11 | 14
AO | B11 | 15
AO | B11 | 16
DI | B12 | 9
DI | B12 | 10
DI | B12 | 11
DI | B12 | 12
DI | B12 | 13
DI | B12 | 14
DI | B12 | 15
DI | B12 | 16
AI | B12 | 1 |  | PT5004
AI | B12 | 2 |  | PT5a10
AI | B12 | 3 |  | PT5b10
AI | B12 | 4 |  | PT5c10
AI | B12 | 5 |  | PT5d10
AI | B12 | 6 |  | PT5018
AI | B12 | 7 |  | LT4a54
AI | B12 | 8 |  | LT4b54
AI | B12 | 9
AI | B12 | 10
AI | B12 | 11
AI | B12 | 12
AI | B12 | 13
AI | B12 | 14
AI | B12 | 15
AI | B12 | 16

## Terminals
Name-old | Name | Terminal ref | Terminal number | [10 empty] | Avaliable patch panel connectors:
| EH1a02 | XP1 | 1 | 2 |  |  |  | Each heater has its own cable. I need to take one apart to confirm the details. | [5 empty] | 28 pin outputs | 3
| EH1a04 |  | 3 | 4 | [9 empty] | 28 pin inputs | 4
| EH1a24 |  | 5 | 6 | [9 empty] | 14 pin outputs | 6
| EH4a54 |  | 7 | 8 | [9 empty] | 14 pin inputs
| EH1a02 |  | 9 | 10
| EH1a04 |  | 11 | 12
| EH1a24 |  | 13 | 14
| EH4a54 |  | 15 | 16
| LP1a02 | XP2 | 1 | 2 | 3 | PE |  | LP1a02 cable | 5x1.5mm2 | 1 | 2 | 3 | 4
| LP1b02 |  | 4 | 5 | 6 | PE |  | LP1b02 cable | 5x1.5mm3 | 1 | 2 | 3 | 4
| GP5020 | XP3 | 1 | 2 | 3 | PE |  | GP5020 cable | 5x4mm2 | 1 | 2 | 3 | 4
| HX5002 |  | 1 | 2 | PE |  |  | HX5002 cable | 3x1.5mm2 | 1 | 2 | 3
| CV5e12 | [6 empty] | Carel valve cable | N12 | 1 | 2 | 3 | 4
| CV5f14 | [8 empty] | 5 | 6 | 7 | 8
TL_VL102 | EV9a60 | XDI1 | B0.0 | B0.1 | B0.2 |  |  | EV9a60 cable | N12 | 2 | 4 | 9
TL_VL111 | EV1a08 |  | B0.3 | B0.4 | B0.5 | B0.6 |  | EV1a08 cable | N12 | 2 | 4 | 6 | 9
TL_VL104 | EV4a54 |  | B0.7 | B1.0 | B1.1 |  |  | EV4a54 cable | N12 | 2 | 4 | 9
TL_VL109 | EV1a21 |  | B1.2 | B1.3 | B1.4 |  |  | EV1a21 cable | N12 | 2 | 4 | 9
TR_VL104 | EV4b54 |  | B1.5 | B1.6 | B1.7 |  |  | EV4b54 cable | N12 | 2 | 4 | 9
TR_VL109 | EV1b21 |  | B2.0 | B2.1 | B2.2 |  |  | EV1b21 cable | N12 | 2 | 4 | 9
TR_VL102 | EV9b60 |  | B2.3 | B2.4 | B2.5 |  |  | EV9b60 cable | N12 | 2 | 4 | 9
TR_VL111 | EV1b08 |  | B2.6 | B2.7 | B3.0 | B3.1 |  | EV1b08 cable | N12 | 2 | 4 | 6 | 9
| Spare |  | B3.2 | B3.3 | B3.4 | B3.5
|  |  | B3.6 | B3.7
| TS_A_OK | XDI2 | B0.0 |  |  |  |  | CO2 safety chain | N12 | 1 | 2
| TS_B_OK |  | B0.1 | [6 empty] | 3 | 4
| LP1a02_TS |  | B0.2 | [6 empty] | 5 | 6
| LP1b02_TS |  | B0.3 | [6 empty] | 7 | 8
| GP5020_TS |  | B0.4 |  |  |  |  | Chiller TT cable 2 | N12 | 9 | 10
| PS1a02 |  | B0.5 |  |  |  |  | CO2 safety | N12 | 9 | 10
| PS1b02 |  | B0.6 | [6 empty] | 11 | 12
| EMS_OK |  | B0.7
| 3P_Volt_OK |  | B1.0
B1.1
|  |  | B1.2 | B1.3 | B1.4
|  |  | B1.5 | B1.6 | B1.7 | B2.0 | B2.1
| Spare |  | B2.2 | B2.3 | B2.4 | B2.5 | B2.6
|  |  | B2.7 | B3.0 | B3.1 | B3.2 | B3.3
|  |  | B3.4 | B3.5 | B3.6 | B3.7
| GP5020_CB_OK | XDI3 | B0.0 |  |  |  |  | Internal cabinet signals
| HX5002_CB_OK |  | B0.1
| LT_CB_OK |  | B0.2
| 24VDC_CB_OK |  | B0.3
| LP1a02_CB_OK |  | B0.4
| LP1b02_CB_OK |  | B0.5
| 24VAC_CB_OK |  | B0.6
| EHA_CB_OK |  | B0.7
| EHB_CB_OK |  | B1.0
| Cab_CB_OK |  | B1.1
| Phase_CB_OK |  | B1.2
| CO2A_DC_CB_OK |  | B1.3
| CO2B_DC_CB_OK |  | B1.4
| Chill_DC_CB_OK |  | B1.5
| EMS_DC_CB_OK |  | B1.6
| Cabinet_DC_CB_OK |  | B1.7
| EHA_DI |  | B2.0
| EHB_DI |  | B2.1
| LP1a02_DI |  | B2.2
| LP1b02_DI |  | B2.3
| GP5020_DI |  | B2.4
| HX5002_DI |  | B2.5
| 24VDC_OK |  | B2.6
| PS5020_L |  | B2.7
| PS5020_OK |  | B3.0
| PS5020_H |  | B3.1
| CV5e12_OK |  | B3.2
| CV5f14_OK |  | B3.3
B3.4
| Spare |  | B3.5
B3.6
B3.7
TL_VL102 | EV9a60 | XDO1 | 0.14 | 1.24 |  |  |  | EV9a60 cable | N12 | 1 | 3
TL_VL111 | EV1a08 |  | 2.34 | 3.44 | 4.54 |  |  | EV1a08 cable | N12 | 1 | 3 | 5
TL_VL104 | EV4a54 |  | 5.64 | 6.74 |  |  |  | EV4a54 cable | N12 | 1 | 3
TL_VL109 | EV1a21 |  | 7.84 | 0.94 |  |  |  | EV1a21 cable | N12 | 1 | 3
TR_VL104 | EV1b21 |  | 1.104 | 2.114 |  |  |  | EV1b21 cable | N12 | 1 | 3
TR_VL109 | EV4b54 |  | 3.124 | 4.134 |  |  |  | EV4b54 cable | N12 | 1 | 3
TR_VL102 | EV9b60 |  | 5.144 | 6.154 |  |  |  | EV9b60 cable | N12 | 1 | 3
TR_VL111 | EV1b08 |  | 7.164 |  |  |  |  | EV1b08 cable | N12 | 1
| EV1b08 | XDO2 | 0.174 | 1.184 | [6 empty] | 3 | 5
| EH1a02 |  | 2.194 |  |  |  |  | Internal cabinet signals
| EH1a04 |  | 3.204
| EH1a24 |  | 4.214
| EH4a54 |  | 5.224
| EH1b02 |  | 6.234
| EH1b04 |  | 7.244
| EH1b24 |  | 0.254
| EH4b54 |  | 1.267
| LP1a02 |  | 2.274
| LP1b02 |  | 3.284
| GP5020 |  | 4.294
| HX5002 |  | 5.304
| EHA |  | 6.314
| EHB |  | 7.324
| Spare | XDO3 | 0.11 | 0.12
|  |  | 1.21 | 1.22
|  |  | 2.31 | 2.32
|  |  | 3.41 | 3.42
|  |  | 4.51 | 4.52
|  |  | 5.61 | 5.62
|  |  | 6.71 | 6.72
|  |  | 7.81 | 7.82
|  |  | 0.91 | 0.92
|  |  | 1.101 | 1.102
|  |  | 2.111 | 2.112
|  |  | 3.121 | 3.122
|  |  | 4.131 | 4.132
|  |  | 5.141 | 5.142
|  |  | 6.151 | 6.152
|  |  | 7.161 | 7.162
| Spare | XDO4 | 0.171 | 0.172
|  |  | 1.181 | 1.182
|  |  | 2.191 | 2.192
|  |  | 3.201 | 3.202
|  |  | 4.211 | 4.212
|  |  | 5.221 | 5.222
|  |  | 6.231 | 6.232 | 7.241 | 7.242
|  |  | 0.251 | 0.252 | 1.261 | 1.262
|  |  | 2.271 | 2.272 | 3.281 | 3.282
|  |  | 4.291 | 4.292 | 5.301 | 5.302
|  |  | 6.311 | 6.312 | 7.321 | 7.322
| CO2A_DC_CB_DO | XDO5 | 3
| CO2B_DC_CB_DO |  | 4
| Chill_DC_CB_DO |  | 5
| EMS_DC_CB_DO |  | 6
| Cabinet_DC_CB_DO |  | 7
| EX5a08 |  | 8 |  |  |  |  | XS1 | 0.11 | 0.14 |  | Cabinet SSRs |  | Expansion valve cable | N12 | 1 | 2
| EX5b08 |  | 9 | [5 empty] | 1.11 | 1.14 | [5 empty] | 3 | 4
| EX5c08 |  | 10 | [5 empty] | 2.11 | 2.14 | [5 empty] | 5 | 6
| EX5d08 |  | 15 | [5 empty] | 3.11 | 3.14 | [5 empty] | 7 | 8
16
17
18
19
20
21
22
27
28
29
30
31
32
33
34
39
|  |  | 40 | 41 | 42 | 43 | 44
|  |  | 45 | 46
| Shorted | XAI1 | 1 | 2
| NC |  | 3
| 24V |  | 4
| NC |  | 5
| TT1a02 |  | 6 | 7
|  |  | 8 | 9
| NC |  | 10
| TT1a10 |  | 11 | 12
|  |  | 13 | 14
| NC |  | 15
| TT1a16 |  | 16 | 17
|  |  | 18 | 19
| NC |  | 20
| TT9a52 |  | 21 | 22
|  |  | 23 | 24
| NC |  | 25 | 26 | 27
| TT9a56 |  | 28 | 29
|  |  | 30 | 31
| NC |  | 32
| TT9a68 |  | 33 | 34
|  |  | 35 | 36
| NC |  | 37
| PT1a04 |  | 38 | 39
| PT1a16 |  | 40 | 41
| NC |  | 42
| PT9a52 |  | 43 | 44
| PT9a66 |  | 45 | 46
| NC |  | 47
| 0V |  | 48
| NC |  | 49 | 50
| Shorted | XAI2 | 1 | 2
| NC |  | 3
| 24V |  | 4
| NC |  | 5
| TT1b02b |  | 6 | 7 | 8 | 9
| NC |  | 10
| TT1b10 |  | 11 | 12 | 13 | 14
| NC |  | 15
| TT1b16 |  | 16 | 17 | 18 | 19
| NC |  | 20
| TT9b52 |  | 21 | 22 | 23 | 24
| NC |  | 25 | 26 | 27
| TT9b56 |  | 28 | 29 | 30 | 31
| NC |  | 32
| TT9b68 |  | 33 | 34 | 35 | 36
| NC |  | 37
| PT1b04 |  | 38 | 39
| PT1b16 |  | 40 | 41
| NC |  | 42
| PT9b52 |  | 43 | 44
| PT9b66 |  | 45 | 46
| NC |  | 47
| 0V |  | 48
| NC |  | 49 | 50
| Shorted | XAI3 | 1 | 2
| NC |  | 3
| 24V |  | 4
| NC |  | 5
| PT5a10 |  | 6 | 7
TempRack (PT100) | PT5c10 |  | 8 | 9
| NC |  | 10
TL_TT121 | TT2a02 |  | 11 | 12
TL_TT122 | TT1a04 |  | 13 | 14
| NC |  | 15
TL_TT123 | TT1a24 |  | 16 | 17
TL_TT124 | TT4a54 |  | 18 | 19
| NC |  | 20
TL_TT125 | TT2b02 |  | 21 | 22
TR_TT121 | TT1b04 |  | 23 | 24
| NC |  | 25 | 26 | 27
TR_TT122 | TT1b24 |  | 28 | 29
TR_TT123 | TT4b54 |  | 30 | 31
| NC |  | 32
TR_TT124 |  |  | 33 | 34
TR_TT125 |  |  | 35 | 36
| NC |  | 37
TLR-TT122 |  |  | 38 | 39
|  |  | 40 | 41
| NC |  | 42
| TT5c16 |  | 43 | 44 | 45 | 46
| NC |  | 47
| 0V |  | 48
| NC |  | 49 | 50
| Shorted | XAI4 | 1 | 2
| NC |  | 3
| 24V |  | 4
| NC |  | 5
| TT5002 |  | 6 | 7 | 8 | 9
| NC |  | 10
| TT5004 |  | 11 | 12 | 13 | 14
| NC |  | 15
| TT5006 |  | 16 | 17 | 18 | 19
| NC |  | 20
| TT5a10 |  | 21 | 22 | 23 | 24
| NC |  | 25 | 26 | 27
| TT5b10 |  | 28 | 29 | 30 | 31
| NC |  | 32
| TT5c10 |  | 33 | 34 | 35 | 36
| NC |  | 37
| TT5d10 |  | 38 | 39 | 40 | 41
| NC |  | 42
| TT5018 |  | 43 | 44 | 45 | 46
| NC |  | 47
| 0V |  | 48
| NC |  | 49 | 50
| Shorted | XFM1 (DI and AO) | 1 | 2
| 24V |  | 3
| DI |  | 4 | 5 | 6 | 7 | 8
| DI |  | 9 | 10 | 11
| NC |  | 12
| CV5e12 |  | 13 | 14
| CV5f14 |  | 15 | 16
| AO |  | 17 | 18 | 19 | 20
| AO |  | 21 | 22 | 23 | 24
| AO |  | 25 | 26 | 27 | 28
| NC |  | 29 | 30
| AO |  | 31 | 32 | 33 | 34
| AO |  | 35 | 36 | 37 | 38
| AO |  | 39 | 40 | 41 | 42
| AO |  | 43 | 44 | 45 | 46
| NC |  | 47
| 0V |  | 48
| NC |  | 49 | 50
| Shorted | XFM2 (DI and AI) | 1 | 2
| 24V |  | 3
| DI |  | 4 | 5 | 6 | 7 | 8
| DI |  | 9 | 10 | 11
1 | PT5004 |  | 12 | 13 |  |  |  | Chiller PT (32W1) | N12 | 1 | 2
2 | PT5b10 |  | 14 | 15 | [5 empty] | 3 | 4
3 | PT5d10 |  | 16 | 17 | [5 empty] | 5 | 6
4 | PT5018 |  | 18 | 19 | [5 empty] | 7 | 8
5 | PT4a54 |  | 20 | 21 | [5 empty] | 9 | 10
6 | PT4b54 |  | 22 | 23 | [5 empty] | 11 | 12
7 | LT4a54 |  | 24 | 25
8 | LT4b54 |  | 26 | 27
Reference Junction | IC |  | 28 | 29
| Comp |  | 30 | 31
| AI |  | 32 | 33 | 34 | 35
| AI |  | 36 | 37 | 38 | 39
| AI |  | 40 | 41 | 42 | 43
| AI |  | 44 | 45 | 46 | 47
| 0V |  | 48
| NC |  | 49 | 50

## Cables
Cable number | Description | Type | Pin |  |  |  | Description |  | 512 | 512
| Side A TT | 28 | 1 | 2 | 3 | 4 | TT1a02 |  | 514 | 513
|  |  | 5 | 6 | 7 | 8 | TT1a10 |  | 516 | 514
|  |  | 9 | 10 | 11 | 12 | TT9a56 |  | 518 | 515
|  |  | 13 | 14 | 15 | 16 | TT9a68 |  | 520 | 516
|  |  | 17 | 18 | 19 | 20 | TT5a10 |  | 522 | 517
|  |  | 21 | 22 | 23 | 24 |  |  | 524 | 518
|  |  | 25 | 26 | 27 | 28 |  |  | 526 | 519
| Side B TT | 28 | 1 | 2 | 3 | 4 | TT1b02 |  | 528 | 520
|  |  | 5 | 6 | 7 | 8 | TT1b10 |  | 530 | 521
|  |  | 9 | 10 | 11 | 12 | TT9b56 |  | 532 | 522
|  |  | 13 | 14 | 15 | 16 | TT9b68 |  | 534 | 523
|  |  | 17 | 18 | 19 | 20 | TT5c10 |  | 536 | 524
|  |  | 21 | 22 | 23 | 24 |  |  | 538 | 525
|  |  | 25 | 26 | 27 | 28 |  |  | 540 | 526
| CO2 PT | [5 empty] | PT1a04 | PT9a66
[7 empty] | PT5a10 | PT1b04
[7 empty] | PT9b66 | PT5c10
| CO2 Safety | 12 | 1 | 2 | 3 | 4 | LP1a02_PS | LP1a02_TS | 542 | 527
|  |  | 5 | 6 | 7 | 8 | TS_A | LP1b02_PS |  | 528
|  |  | 9 | 10 | 11 | 12 | LP1b02_TS | TS_C |  | 529
| Chiller TT | 28 | 1 | 2 | 3 | 4 | TT5002 |  |  | 530
|  |  | 5 | 6 | 7 | 8 | TT5004 |  |  | 531
|  |  | 9 | 10 | 11 | 12 | TT5006 |  |  | 532
|  |  | 13 | 14 | 15 | 16 | TT5b10 |  |  | 533
|  |  | 17 | 18 | 19 | 20 | TT5d10 |  |  | 534
|  |  | 21 | 22 | 23 | 24 | TT5c16 |  |  | 535
|  |  | 25 | 26 | 27 | 28 | TT5018 |  |  | 536
| Chiller PT | 12 | 1 | 2 | 3 | 4 | PT5004 | PT5b10 |  | 537
|  |  | 5 | 6 | 7 | 8 | PT5d10 | PT5018 |  | 538
|  |  | 9 | 10 | 11 | 12 | PT4a54 | PT4b54 |  | 539
| Carel Valves | 12 | 1 | 2 | 3 | 4 | CV5e12 |  |  | 540
|  |  | 5 | 6 | 7 | 8 | CV5f14 |  |  | 541
|  |  | 9 | 10 | 11 | 12 | GP5020_TS |  |  | 542
| Expansion valves | 12 | 1 | 2 | 3 | 4 | CV5a08 | CV5b08 |  | 543
|  |  | 5 | 6 | 7 | 8 | CV5c08 | CV5d08
|  |  | 9 | 10 | 11 | 12 | TS_A | TS_C
| Compressor pressure switch | 5x1.5 | 1 | 2 | 3 | 4 | GP5020_PS
5
| TC - CO2 | 6x TC wire
| TC - Chiller | 2x TC wire
Power cables
Compressor |  | 4x4m2
Fan |  | 3x1.5mm2
Pumps |  | 4x1.5mm2
Heaters |  | 3x2.5mm2

## Power
Device | Electrical panel | Rack patch panel | Pin number | Connection | Comments
EH1a02 |  | XR20 | 1 | Live
|  |  | 2 | Neutral
|  |  | 3 | NC
|  |  | 4 | Ground
|  |  | 5 | NC
EH1a04 |  | XR21 | 1 | Live
|  |  | 2 | Neutral
|  |  | 3 | NC
|  |  | 4 | Ground
|  |  | 5 | NC
EH1a24 |  | XR22 | 1 | Live
|  |  | 2 | Neutral
|  |  | 3 | NC
|  |  | 4 | Ground
|  |  | 5 | NC
EH4a54 |  | XR23 | 1 | Live
|  |  | 2 | Neutral
|  |  | 3 | NC
|  |  | 4 | Ground
|  |  | 5 | NC
EH1a02 |  | XR24 | 1 | Live
|  |  | 2 | Neutral
|  |  | 3 | NC
|  |  | 4 | Ground
|  |  | 5 | NC
EH1a04 |  | XR25 | 1 | Live
|  |  | 2 | Neutral
|  |  | 3 | NC
|  |  | 4 | Ground
|  |  | 5 | NC
EH1a24 |  | XR26 | 1 | Live
|  |  | 2 | Neutral
|  |  | 3 | NC
|  |  | 4 | Ground
|  |  | 5 | NC
EH4a54 |  | XR27 | 1 | Live
|  |  | 2 | Neutral
|  |  | 3 | NC
|  |  | 4 | Ground
|  |  | 5 | NC
LP1a02 |  |  | 1
2
3
4
5
6
7
8
9
10
LP1b02 |  |  | 1
2
3
4
5
6
7
8
9
10

## Valve-wiring
Connector pin | colour | 2 way valve pin |  | 3 way valve pin
1 | Brown | 1 | Open | 1 | Port 1
2 | Red | 2 | Open feedback | 2 | Port 1 FB
3 | Orange | 3 | Close | 3 | Centre/closed
4 | Yellow | 4 | Close feedback | 4 | Centre/closed FB
5 | Green | NC |  | 5 | Port 2
6 | Blue | NC |  | 6 | Port 2 FB
7 | Purple | NC |  | NC
8 | Grey | NC |  | NC
9 | White | 9 | Motor running | 9 | Motor run FB
10 | Black | 10 | Common | 10 | Common
11 | Pink | NC |  | NC
12 | Blue/Brown | PE |  | PE

## TT
New part | Old Code | low | high | Part number | Function
?? | TL_TT121 | 0 | 100 | Thermocouple K | Press damper temperature
?? | TR_TT121 | 0 | 100 | Thermocouple K | Press damper temperature
TT1a02a | TL_TT122 | 12 | 25 | Thermocouple K | TL-HT102 Control (pump.state oil heater)
TT1a02b | TL_TT115 | -45 | -2 | PT100 | TL-PM101 pump.state outlet
TT1a04 | TL_TT123 | 0 | 100 | Thermocouple K | TL-HT103 Control
TT1a10 | TL_TT120 | -48 | 30 | PT100 | Transfer tube liquid inlet
TT1a16 |  |  |  |  | CO2 liquid temperature
TT1b16 |  |  |  |  | CO2 liquid temperature
TT1a24 | TL_TT124 | -45 | 50 | Thermocouple K | TL-HT104 Control
TT1b02a | TR_TT122 | 12 | 25 | Thermocouple K | TR-HT102 Control (pump.state oil heater)
TT1b02b | TR_TT115 | -45 | -2 | PT100 | TR-PM101 pump.state outlet
TT1b04 | TR_TT123 | 0 | 100 | Thermocouple K | TR-HT103 Control
TT1b10 | TR_TT120 | -48 | 30 | PT100 | Transfer tube liquid inlet
TT1b24 | TR_TT124 | -45 | 50 | Thermocouple K | TR-HT104 Control
TT4a54 | TL_TT125 | -45 | 100 | Thermocouple K | TL-HT105 Control (Accu heater)
TT4b54 | TR_TT125 | -45 | 100 | Thermocouple K | TR-HT105 Control (Accu heater)
TT5002 |  |  |  |  | Compressor outlet temperature
TT5004 |  |  |  |  | Condensor outlet temperature
TT5006 |  |  |  |  | Liquid freon temperature
TT5018 |  |  |  |  | Compressor inlet temperature
TT5a10 |  |  |  |  | Evaporator outlet temperature
TT5b10 |  |  |  |  | Evaporator outlet temperature
TT5c10 |  |  |  |  | Evaporator outlet temperature
TT5d10 |  |  |  |  | Evaporator outlet temperature
TT5c16 |  |  |  |  | Feedback line temperature
TT9a52 |  |  |  |  | CO2 return temperature
TT9b52 |  |  |  |  | CO2 return temperature
TT9a56 | TL_TT101 | -45 | 5 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | Transfer tube vapor outlet
TT9a68 | TL_TT112 | -48 | -2 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | TL-PM101 pump.state inlet
TT9b56 | TR_TT101 | -45 | 5 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | Transfer tube vapor outlet
TT9b68 | TR_TT112 | -48 | -2 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | TR-PM101 pump.state inlet
| TL_TT113 | -40 | 30 | PT100 | TL-PM101 pump.state head oil side
| TL_TT114 | -40 | 30 | PT100 | TL-PM101 pump.state head CO2 side
| TL_TT116 | -45 | -2 | PT100 | liquid line
| TL_TT117 | -45 | 30 | PT100 | By-pass liquid
| TR_TT113 | -40 | 30 | PT100 | TR-PM101 pump.state head oil side
| TR_TT114 | -40 | 30 | PT100 | TR-PM101 pump.state head CO2 side
| TR_TT116 | -45 | -2 | PT100 | liquid line
| TR_TT117 | -45 | 30 | PT100 | By-pass liquid
| TL_TT107 | -45 | 5 | PT100 | Accumulator line
| TL_TT108 | -20 | 5 | PT100 | Accumulator Liquid
| TL_TT109 | -5 | 20 | PT100 | Accumulator Vapor
| TR_TT107 | -45 | 5 | PT100 | Accumulator line
| TR_TT108 | -20 | 5 | PT100 | Accumulator Liquid
| TR_TT109 | -5 | 20 | PT100 | Accumulator Vapor
| TL_TT118 | -45 | 30 | PT100 | By-pass vapor
| TL_TT104 | -48 | 5 | PT100 | Back-up condeser inlet
| TL_TT119 | -48 | 30 | PT100 | Condenser Back plate
| TL_TT106 | -48 | 5 | PT100 | Back-up condeser outlet
| TL_TT110 | -48 | -2 | PT100 | Condenser outlet
| TR_TT118 | -45 | 30 | PT100 | By-pass vapor
| TR_TT104 | -48 | 5 | PT100 | Back-up condeser inlet
| TR_TT102 | -48 | 30 | PT100 | Main condenser Front plate
| TR_TT106 | -48 | 5 | PT100 | Back-up condeser outlet
| TR_TT110 | -48 | -2 | PT100 | Condenser outlet
| TL_TT102 | -48 | 30 | PT100 | Main condenser Front plate
| TL_TT103 | -48 | 5 | PT100 | Main condenser inlet
| TL_TT105 | -48 | 5 | PT100 | Main condenser outlet
| TR_TT103 | -48 | 5 | PT100 | Main condenser inlet
| TR_TT105 | -48 | 5 | PT100 | Main condenser outlet
| TR_TT111 | -5 | 10 | PT100 | TLR-PM101 pump.state head cooling
| PA_TT101 | 4 | 15 | PT100 | Cooling water inlet
| PA_TT102 | 4 | 15 | PT100 | Cooling water outlet
| PB_TT101 | 12 | 35 | PT100 | Air inlet
| SA_TT101 | 15 | 25 | PT100 | Discharge
| SA_TT102 | 4 | 25 | PT100 | Condensor outlet
| SA_TT103 | 12 | 25 | PT100 | Liquid vessel inlet
| SA_TT104 | 12 | 25 | PT100 | Liquid vessel
| SA_TT105 | 12 | 25 | PT100 | Liquid
| SA_TT106 | -45 | 25 | PT100 | SA-HX103 subcooled liquid
| SA_TT107 | -45 | 25 | PT100 | SA-HX103 evaporator inlet
| SA_TT108 | -45 | 25 | PT100 | SA-HX103 evaporator outlet
| SA_TT109 | -45 | 25 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | SA-HX103 superheat
| SA_TT110 | -45 | 25 | PT100 | SA-HX105 subcooled liquid
| SA_TT111 | -45 | 25 | PT100 | SA-HX105 evaporator inlet
| SA_TT112 | -45 | 25 | PT100 | SA-HX105 evaporator outlet
| SA_TT113 | -45 | 25 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | SA-HX105 superheat
| SA_TT114 | -35 | 25 | PT100 | SA-HX107/108 subcooled liquid
| SA_TT115 | -35 | 25 | PT100 | SA-HX107 evaporator inlet
| SA_TT116 | -35 | 25 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | SA-HX107 superheat
| SA_TT117 | -35 | 25 | PT100 | SA-HX108 evaporator inlet
| SA_TT118 | -35 | 25 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | SA-HX108 superheat
| SA_TT119 | -35 | 25 | PT100 | SA-HX107/108 cold gas
| SA_TT120 | -35 | 25 | PT100 | SA-HX107/108 Suction
| SA_TT121 | -35 | 25 | PT100 | Suction
| SA_TT122 | 12 | 60 | PT100 | Compressor
| SB_TT101 | 15 | 100 | PT100 | Discharge
| SB_TT102 | 4 | 35 | PT100 | Condensor outlet
| SB_TT104 | 12 | 35 | PT100 | Liquid vessel
| SB_TT105 | 12 | 35 | PT100 | Liquid
| SB_TT107 | -35 | 25 | PT100 | SB-HX103 evaporator inlet
| SB_TT109 | -35 | 25 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | SB-HX103 superheat
| SB_TT111 | -35 | 25 | PT100 | SB-HX105 evaporator inlet
| SB_TT113 | -35 | 25 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | SB-HX105 superheat
| SB_TT114 | -25 | 25 | PT100 | subcooled liquid
| SB_TT115 | -25 | 25 | PT100 | SB-HX107 evaporator inlet
| SB_TT116 | -25 | 25 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | SB-HX107 superheat
| SB_TT117 | -25 | 25 | PT100 | SB-HX108 evaporator inlet
| SB_TT118 | -25 | 25 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | SB-HX108 superheat
| SB_TT119 | -25 | 25 | PT100 | Cold gas
| SB_TT121 | -25 | 25 | PT100 | Suction
| SB_TT122 | 12 | 25 | PT100 | Compressor
| TL_TT001 | -35 | 10 | PT100 | TL_HX001 Liquid inlet
| TL_TT002 | -35 | 10 | PT100 | TL_HX001 block 1
| TL_TT003 | -35 | 10 | PT100 | TL_HX001Dry-out monitoring
| TL_TT004 | -35 | 10 | PT100 | TL_HX001 Vapor outlet
| TL_TT005 | -35 | 10 | PT100 | TL_HX002 Dry-out monitoring
| TL_TT006 | -35 | 10 | PT100 | TL_HX003 Dry-out monitoring
| TL_TT007 | -35 | 10 | PT100 | TL_HX004 Dry-out monitoring
| TL_TT008 | -35 | 10 | PT100 | TL_HX005 Dry-out monitoring
| TL_TT009 | -35 | 10 | PT100 | TL_HX006 Dry-out monitoring
| TL_TT010 | -35 | 10 | PT100 | TL_HX007 Dry-out monitoring
| TL_TT011 | -35 | 10 | PT100 | TL_HX008 Dry-out monitoring
| TL_TT012 | -35 | 10 | PT100 | TL_HX009 Dry-out monitoring
| TL_TT013 | -35 | 10 | PT100 | TL_HX010 Dry-out monitoring
| TL_TT014 | -35 | 10 | PT100 | TL_HX011 Dry-out monitoring
| TL_TT015 | -35 | 10 | PT100 | TL_HX012 Liquid inlet
| TL_TT016 | -35 | 10 | PT100 | TL_HX012 block 1
| TL_TT017 | -35 | 10 | PT100 | TL_HX012 Dry-out monitoring
| TL_TT018 | -35 | 10 | PT100 | TL_HX012 Vapor outlet
| TL_TT019 | -35 | 10 | PT100 | TL_HX013 Dry-out monitoring
| TL_TT020 | -35 | 10 | PT100 | TL_HX014 Dry-out monitoring
| TL_TT021 | -35 | 10 | PT100 | TL_HX015 Dry-out monitoring
| TL_TT022 | -35 | 10 | PT100 | TL_HX016 Dry-out monitoring
| TL_TT023 | -35 | 10 | PT100 | TL_HX017 Dry-out monitoring
| TL_TT024 | -35 | 10 | PT100 | TL_HX018 Dry-out monitoring
| TL_TT025 | -35 | 10 | PT100 | TL_HX021Dry-out monitoring
| TL_TT026 | -35 | 10 | PT100 | TL_HX024 Dry-out monitoring
| TL_TT027 | -35 | 10 | PT100 | TL_HX025 Dry-out monitoring
| TL_TT028 | -35 | 10 | PT100 | TL_HX026 Dry-out monitoring
| TL_TT029 | -35 | 10 | PT100 | TL_HX027 Liquid inlet
| TL_TT030 | -35 | 10 | PT100 | TL_HX027 block 1
| TL_TT031 | -35 | 10 | PT100 | TL_HX027 Dry-out monitoring
| TL_TT032 | -35 | 10 | PT100 | TL_HX027 Vapor outlet
| TL_TT033 | -35 | 10 | PT100 | Vapor return
| TL_TT034 | -35 | 10 | PT100 | Vapor return
| TL_TT035 | -35 | 20 | PT100 | Manifold
| TL_TT036 | 12 | 30 | PT100 | Bellow flange
| TL_TT037 | 15 | 27 | PT100 | TL_HT001 Heater Control
| TL_TT038 | 15 | 27 | PT100 | TL_HT002 Heater Control
| TL_TT039 | 15 | 27 | PT100 | TL_HT003 Heater Control
| TL_TT040 | 15 | 27 | PT100 | TL_HT004 Heater Control
| TL_TT041 | 15 | 27 | PT100 | Module base
| TL_TT042 | 15 | 27 | PT100 | Module base
| TL_TT043 | 15 | 27 | PT100 | RF-Foil
| TL_TT044 | 15 | 27 | PT100 | RF-Foil
| TL_TT045 | -35 | 30 | PT100 | Transfer tube liquid outlet
| TL_TT046 | -35 | 10 | PT100 | Local control box liquid inlet
| TL_TT047 | -35 | 10 | PT100 | Capillaries inlet
| TL_TT048 | -35 | 10 | PT100 | Local control box vapor outlet
| TR_TT119 | -48 | 30 | PT100 | Condenser Back plate
| TLR_TT112 | -35 | 10 | Internal PT100 Rodax: PPA_PT100_SO_S_A1_D3_W4_130_6D | TLR-PM101 pump.state inlet
| TLR_TT113 | -35 | 10 | PT100 | TLR-PM101 pump.state head oil side
| TLR_TT114 | -35 | 10 | PT100 | TLR-PM101 pump.state head CO2 side
| TLR_TT115 | -35 | 10 | PT100 | TLR-PM101 pump.state outlet
| TLR_TT122 | -45 | 80 | Thermocouple K | TLR-HT102 Control (pump.state oil heater)
| TR_TT001 | -35 | 10 | PT100 | TR_HX001 Liquid inlet
| TR_TT002 | -35 | 10 | PT100 | TR_HX001 block 1
| TR_TT003 | -35 | 10 | PT100 | TR_HX001Dry-out monitoring
| TR_TT004 | -35 | 10 | PT100 | TR_HX001 Vapor outlet
| TR_TT005 | -35 | 10 | PT100 | TR_HX002 Dry-out monitoring
| TR_TT006 | -35 | 10 | PT100 | TR_HX003 Dry-out monitoring
| TR_TT007 | -35 | 10 | PT100 | TR_HX004 Dry-out monitoring
| TR_TT008 | -35 | 10 | PT100 | TR_HX005 Dry-out monitoring
| TR_TT009 | -35 | 10 | PT100 | TR_HX006 Dry-out monitoring
| TR_TT010 | -35 | 10 | PT100 | TR_HX007 Dry-out monitoring
| TR_TT011 | -35 | 10 | PT100 | TR_HX008 Dry-out monitoring
| TR_TT012 | -35 | 10 | PT100 | TR_HX009 Dry-out monitoring
| TR_TT013 | -35 | 10 | PT100 | TR_HX010 Dry-out monitoring
| TR_TT014 | -35 | 10 | PT100 | TR_HX011 Dry-out monitoring
| TR_TT015 | -35 | 10 | PT100 | TR_HX012 Liquid inlet
| TR_TT016 | -35 | 10 | PT100 | TR_HX012 block 1
| TR_TT017 | -35 | 10 | PT100 | TR_HX012 Dry-out monitoring
| TR_TT018 | -35 | 10 | PT100 | TR_HX012 Vapor ouTRet
| TR_TT019 | -35 | 10 | PT100 | TR_HX013 Dry-out monitoring
| TR_TT020 | -35 | 10 | PT100 | TR_HX014 Dry-out monitoring
| TR_TT021 | -35 | 10 | PT100 | TR_HX015 Dry-out monitoring
| TR_TT022 | -35 | 10 | PT100 | TR_HX016 Dry-out monitoring
| TR_TT023 | -35 | 10 | PT100 | TR_HX017 Dry-out monitoring
| TR_TT024 | -35 | 10 | PT100 | TR_HX018 Dry-out monitoring
| TR_TT025 | -35 | 10 | PT100 | TR_HX021Dry-out monitoring
| TR_TT026 | -35 | 10 | PT100 | TR_HX024 Dry-out monitoring
| TR_TT027 | -35 | 10 | PT100 | TR_HX025 Dry-out monitoring
| TR_TT028 | -35 | 10 | PT100 | TR_HX026 Dry-out monitoring
| TR_TT029 | -35 | 10 | PT100 | TR_HX027 Liquid inlet
| TR_TT030 | -35 | 10 | PT100 | TR_HX027 block 1
| TR_TT031 | -35 | 10 | PT100 | TR_HX027 Dry-out monitoring
| TR_TT032 | -35 | 10 | PT100 | TR_HX027 Vapor ouTRet
| TR_TT033 | -35 | 10 | PT100 | Vapor return
| TR_TT034 | -35 | 10 | PT100 | Vapor return
| TR_TT035 | -35 | 20 | PT100 | Manifold
| TR_TT036 | 12 | 30 | PT100 | Bellow flange
| TR_TT037 | 15 | 27 | PT100 | TR_HT001 Heater Control
| TR_TT038 | 15 | 27 | PT100 | TR_HT002 Heater Control
| TR_TT039 | 15 | 27 | PT100 | TR_HT003 Heater Control
| TR_TT040 | 15 | 27 | PT100 | TR_HT004 Heater Control
| TR_TT041 | 15 | 27 | PT100 | Module base
| TR_TT042 | 15 | 27 | PT100 | Module base
| TR_TT043 | 15 | 27 | PT100 | RF-Foil
| TR_TT044 | 15 | 27 | PT100 | RF-Foil
| TR_TT045 | -35 | 30 | PT100 | Transfer tube liquid outlet
| TR_TT046 | -35 | 10 | PT100 | Local control box liquid inlet
| TR_TT047 | -35 | 10 | PT100 | Capillaries inlet
| TR_TT048 | -35 | 10 | PT100 | Local control box vapor outlet
| xx_TTamb | 15 | 25

## PT
New label | Old label | Part Number | Function | Connection | Operating pressure (Bar) | Max Design Pressure (Bar) | Min Design Temperature (C) | Max Design Temperature (C) | Min measuring range (Bar) | Max measuring range (Bar) | Supply (V) | Output signal
PS1a02 | TL_PT103 | Lewa pump integral | TL-PM101 Membrane Pressure |  | 100 | [6 empty] | Open/close
PS1b02 | TR_PT103 | Lewa pump integral | TR-PM101 Membrane Pressure |  | 100 | [6 empty] | Open/close
PS5020_H |  |  | Compressor high pressure switch
PS5020_L |  |  | Compressor low pressure switch
PT1a04 | TL_PT104 | Druck PTX7511-100bar | Pump outlet | G1/4"Female | 100 | 200 | -40 | 80 | 0 | 100 | 9-30Vdc | 4-20mA
PT1a16
PT1b04 | TR_PT104 | Druck PTX7511-100bar | Pump outlet | G1/4"Female | 100 | 200 | -40 | 80 | 0 | 100 | 9-30Vdc | 4-20mA
PT1b16
PT4a54 | TL_PT102 | Druck PTX7511-100bar | Accumulator pressure | G1/4"Female | 100 | 200 | -40 | 80 | 0 | 100 | 9-30Vdc | 4-20mA
PT4b54 | TR_PT102 | Druck PTX7511-100bar | Accumulator pressure | G1/4"Female | 100 | 200 | -40 | 80 | 0 | 100 | 9-30Vdc | 4-20mA
PT5004
PT5018
PT5a10
PT5b10
PT5c10
PT5d10
PT9a52
PT9a66 | TL_PT101 | Druck PTX7511-100bar | Condenser pressure | G1/4"Female | 100 | 200 | -40 | 80 | 0 | 100 | 9-30Vdc | 4-20mA
PT9b52
PT9b66 | TR_PT101 | Druck PTX7511-100bar | Accumulator pressure | G1/4"Female | 100 | 200 | -40 | 80 | 0 | 100 | 9-30Vdc | 4-20mA
| TL_PT001 | Kulite HKM-375M- 100BAR-A | Transfer tune outlet pressure | M10x1 Male | 100 | 200 |  |  | 0 | 100 | 10Vdc | 100mV
| TL_PT002 | Kulite HKM-375M- 100BAR-A | Evaporator inlet pressure | M10x1 Male | 100 | 200 |  |  | 0 | 100 | 10Vdc | 100mV
| TL_PT003 | Kulite HKM-375M- 100BAR-A | Evaporator (outlet) pressure | M10x1 Male | 100 | 200 |  |  | 0 | 100 | 10Vdc | 100mV
| TL_PT004 | Balzers Pirani TPR0118 (DN 16 CF-F) BGG15011 | Tertiary vacuum monitoring | CF16 | 2 |  |  |  | 1.00E- 06 | 1
| TR_PT001 | Kulite HKM-375M- 100BAR-A | Transfer tune outlet pressure | M10x1 Male | 100 | 200 |  |  | 0 | 100 | 10Vdc | 100mV
| TR_PT002 | Kulite HKM-375M- 100BAR-A | Evaporator inlet pressure | M10x1 Male | 100 | 200 |  |  | 0 | 100 | 10Vdc | 100mV
| TR_PT003 | Kulite HKM-375M- 100BAR-A | Evaporator (outlet) pressure | M10x1 Male | 100 | 200 |  |  | 0 | 100 | 10Vdc | 100mV
| TR_PT004 | Balzers Pirani TPR0118 (DN 16 CF-F) BGG15011 | Tertiary vacuum monitoring | CF16 | 2 |  |  |  | 1.00E- 06 | 1
| TLR_PT103 | Lewa pump integral | TLR-PM101 Membrane Pressure |  | 100 | [6 empty] | Open/close
| SA_PT101 | Danfoss AKS 33 60G2051 | Discharge pressure | 1/4" Male Flare | 33 | 55 | 0 | 80 | 0 | 35 |  | 4-20mA
| SA_PT102 | Danfoss AKS 33 60G2051 | Liquid pressure | 1/4" Male Flare | 33 | 55 | 0 | 80 | 0 | 35 |  | 4-20mA
| SA_PT103 | Danfoss AKS 33 60G2048 | Left evaporator pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SA_PT104 | Danfoss AKS 33 60G2048 | Rigth evaporator pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SA_PT105 | Danfoss AKS 33 60G2048 | Left accumulator pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SA_PT106 | Danfoss AKS 33 60G2048 | Right accumulator pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SA_PT107 | Danfoss AKS 33 60G2048 | Suction gas pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SA_PT108 | Danfoss KP15 060-1261 | Compressor protection | 1/4" Male Flare | [7 empty] | Open/close
| SB_PT102 | Danfoss AKS 33 60G2051 | Liquid pressure | 1/4" Male Flare | 33 | 55 | 0 | 80 | 0 | 35 |  | 4-20mA
| SB_PT103 | Danfoss AKS 33 60G2048 | Left evaporator pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SB_PT104 | Danfoss AKS 33 60G2048 | Right evaporator pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SB_PT105 | Danfoss AKS 33 60G2048 | Left accumulator pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SB_PT106 | Danfoss AKS 33 60G2048 | Right accumulator pressure | 1/4" Male Flare | 33 | 33 | -30 | 40 | 0 | 7 |  | 4-20mA
| SB_PT108 | Danfoss KP15 060-1261 | Compressor protection | 1/4" Male Flare | [7 empty] | Open/close
| SB_PT109 |  | Condenser fan speed control

## VL
New code | Code | Part | Function | Connection | Operating pressure (Bar) | Max design pressure (Bar) | Min design temperature (C) | Max design temperature (C) | Pressure setting range (Bar) | Cv (-) | Orifice (mm) | Supply (V) | Power (W) | Electrical Control | Manual Control | Output signal
AV1a22 | TL_VL110 | Swagelok SS31RS4 | Liquid expansion | 1/4" Swagelok | 100 | 212 | -65 | 343 | NA | 0.012 Nom / 0.04 max | 1.6 | NA | NA | NA | Proportiona l | NA
AV1b22 | TR_VL113 | Swagelok SS- 43GHLVCR4 | Transfer tube shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
CV5e12
CV5f14
EV1a08 | TL_VL111 | Swagelok SS- 43GHLVCR4-42dc | Left VTCS shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
EV1a21 | TL_VL109 | Swagelok SS- 43GHLVCR4-42dc | By-pass | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
EV1b08 | TR_VL111 | Swagelok SS- 43GHLVCR4-42dc | Left VTCS shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
EV1b21 | TR_VL109 | Swagelok SS- 43GHLVCR4-42dc | By-pass | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
EV4a54 | TL_VL104 | Swagelok SS- 43GHLVCR4-42dc | Accumulator shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
EV4b54 | TR_VL104 | Swagelok SS- 43GHLVCR4-42dc | Accumulator shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
EV9a60 | TL_VL102 | Swagelok SS- 43GHLVCR4-42dc | Left VTCS shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
EV9b60 | TR_VL102 | Swagelok SS- 43GHLVCR4-42dc | Left VTCS shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
EX5a08 | SB_VL106 | Danfoss AKV 10- 2/068F1164+018F6701 | Evaporator expansion valve and shut-off valve | 3/8"x1/2" solder | 20 | 42 | -60 | 60 | NA |  | 0.6 5
EX5b08 | SB_VL114 | Danfoss AKV 10- 1/068F1161+018F6701 | Evaporator expansion valve and shut-off valve | 3/8"x1/2" solder | 20 | 42 | -60 | 60 | NA |  | 0.5
EX5c08 | SB_VL110 | Danfoss AKV 10-2/068F1164+018F6701 | Expansion valve | 3/8"x1/2" solder | 20 | 42 | -60 | 60 | NA |  | 0.6
EX5d08 | SB_VL119 | Danfoss AKV 10-1/068F1161+018F6701 | Expansion valve | 3/8"x1/2" solder | 20 | 42 | -60 | 60 | NA |  | 0.5
MV1004 | TLR_VL109 | Swagelok SS- 43GXVCR4-42dcx | 3-way Condenser selection | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
MV1010 | TLR_VL110 | Swagelok SS- 43GHLVCR4-42dc | Left-right liquid inter connect | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
MV1a02 | TL_VL107 | Swagelok SS- 43GHLVCR4 | Filling port | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV1a04 | TL_VL108 | Swagelok SS- 43GHLVCR4 | Pump shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV1a12 | TL_VL113 | Swagelok SS- 43GHLVCR4 | Transfer tube shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV1b02 | TR_VL107 | Swagelok SS- 43GHLVCR4 | Filling port | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV1b04 | TR_VL110 | Swagelok SS31RS4 | Liquid expansion | 1/4" Swagelok | 100 | 212 | -65 | 343 | NA | 0.012 Nom / 0.04 max | 1.6 | NA | NA | NA | Proportiona l | NA
MV1b12 | TLR_VL001 | Swagelok SS-4UW-TW | Left right inter connect | 1/4" socket weld | 100 | 172 | -29 | 343 | NA | 0.36 | 4.4 | NA | NA | NA | Proportiona l | NA
MV4a54 | TL_VL105 | Swagelok SS- 43GHLVCR4 | Filling port | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV4b54 | TR_VL105 | Swagelok SS- 43GHLVCR4 | Filling port | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV9066 | TLR_VL101 | Swagelok SS- 43GXVCR4-42dcx | Spare pump | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 0.9 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
MV9a58 | TL_VL101 | Swagelok SS- 43GHLVCR4 | Transfer tube shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV9a68 | TL_VL106 | Swagelok SS- 43GHLVCR4 | Pump shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV9b58 | TR_VL101 | Swagelok SS- 43GHLVCR4 | Transfer tube shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
MV9b68 | TR_VL106 | Swagelok SS- 43GHLVCR4 | Pump shut-off | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | NA | NA | NA | Open/Close | NA
| TL_VL112 | Swagelok SS- 43GHLVCR4-42dc | Liquid vent | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
| TR_VL112 | Swagelok SS- 43GHLVCR4-42dc | Liquid vent | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
| TLR_VL111 | Swagelok SS- 43GHLVCR4-42dc | Left-right vapor inter connect | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
| SA_VL101 | Danfoss GBC10S/009G7051 | Compressor section shut-off | 3/8" solder | 20 | 48 | -40 | 150 | NA
| SA_VL102 | Danfoss NRD/020-1132 | Condenser control | 1/2" solder | 20 | 28 | -45 | 130 | 1.4 - 3
| SA_VL103 | Danfoss/KVR- 12/034L0093 | Condenser pressure control | 1/2" solder | 20 | 28 | -45 | 130 | 5 - 17.5
| SA_VL104 | Integral in SA-AC102 | Liquid line shut-off
| SA_VL106 | Danfoss AKV 10- 2/068F1164+018F6701 | Evaporator expansion valve and shut-off valve | 3/8"x1/2" solder | 20 | 42 | -60 | 60 | NA |  | 0.6 5
| SA_VL107 | Integral in SA-VL108 | Schrader valve |  | 20 | TBV | TBV | TBV | NA
| SA_VL108 | Danfoss GBC12S/009G7052 | Evaporator shut-off | 1/2" solder | 20 | 48 | -40 | 150 | NA
| SA_VL110 | Danfoss AKV 10- 2/068F1164+018F6701 | Expansion valve | 3/8"x1/2" solder | 20 | 42 | -60 | 60 | NA |  | 0.6 5
| SA_VL111 | Integral in SA-VL112 | Schrader valve |  | 20 | TBV | TBV | TBV | NA
| SA_VL112 | Danfoss GBC12S/009G7052 | Evaporator shut-off | 1/2" solder | 20 | 48 | -40 | 150 | NA
| SA_VL114 | Danfoss AKV 10- 1/068F1161+018F6701 | Evaporator expansion valve and shut-off valve | 3/8"x1/2" solder | 20 | 42 | -60 | 60 | NA |  | 0.5
| SA_VL115 | Integral in SA-VL116 | Schrader valve |  | 20 |  |  |  | NA
| SA_VL116 | Danfoss GBC12S/009G7052 | Accu evaporator shut- off | 1/2" solder | 20 | 48 | -40 | 150 | NA
| SA_VL117 | Danfoss KVP-12 | Accu evaporator pressure | 1/2" solder | 18 | 28 | -45 | 130 | 0 - 7 |  | NA
| SA_VL119 | Danfoss AKV 10-1/068F1161+018F6701 | Expansion valve | 3/8"x1/2" solder | 20 | 42 | -60 | 60 | NA |  | 0.5
| SA_VL120 | Integral in SA-VL121 | Schrader valve |  | 20 |  |  |  | NA
| SA_VL121 | Danfoss GBC12S/009G7052 | Accu evaporator shut- off | 1/2" solder | 20 | 48 | -40 | 150 | NA
| SA_VL122 | Danfoss KVP-12 | Accu evaporator pressure | 1/2" solder | 18 | 28 | -45 | 130 | 0 - 7 |  | N A
| SA_VL123 | Danfoss GBC22s/009G7055 | Gas line shut- off | 7/8" solder | 20 | 48 | -40 | 150 | NA
| SA_VL124 | Integral in SA-PM101 | Compressor Suction shut-off
| SA_VL125 | Integral in SA-PM101 | Compressor discharge shut- off
| SA_VL126 | Integral in SA-VL101 | Schrader valve
| SA_VL127 | Integral in SA-VL104 | Schrader valve
| SA_VL128 | Integral in SA-VL123 | Schrader valve
| SB_VL104 | Integral in SB-AC102 | Liquid shut-off line
| SB_VL107 | Integral in SB-VL108 | Schradervalve |  | 20 | TBV | TBV | TBV | NA
| SB_VL108 | Danfoss GBC12S/009G7052 | Evaporator shut-off | 1/2" solder | 20 | 48 | -40 | 150 | NA
| SB_VL111 | Integral in SB-VL112 | Schrader valve |  | 20 | TBV | TBV | TBV | NA
| SB_VL112 | Danfoss GBC12S/009G7052 | Evaporator shut-off | 1/2" solder | 20 | 48 | -40 | 150 | NA
| SB_VL115 | Integral in SB-VL116 | Schrader valve |  | 20 |  |  |  | NA
| SB_VL116 | Danfoss GBC12S/009G7052 | Accu evaporator shut- off | 1/2" solder | 20 | 48 | -40 | 150 | NA
| SB_VL117 | Danfoss KVP-12 | Accu evaporator pressure | 1/2" solder | 18 | 28 | -45 | 130 | 0 - 7 |  | N A
| SB_VL120 | Integral in SB-VL121 | Schrader valve |  | 20 |  |  |  | NA
| SB_VL121 | Danfoss GBC12S/009G7052 | Accu evaporator shut- off | 1/2" solder | 20 | 48 | -40 | 150 | NA
| SB_VL122 | Danfoss KVP-12 | Accu evaporator pressure | 1/2" solder | 18 | 28 | -45 | 130 | 0 - 7 |  | N A
| SB_VL124 | Integral in SB-PM101 | Compressor Suction shut-off
| SB_VL125 | Integral in SB-PM101 | Compressor discharge shut- off
| SB_VL127 | Integral in SB-VL104 | Schrader valve
| SB_VL128 | Integral in SB-VL123 | Schrader valve
| TL_VL001 | Swagelok SS-4UW-TW | Transfer tube shut-off | 1/4" socket weld | 100 | 172 | -29 | 343 | NA | 0.36 | 4.4 | NA | NA | NA | Proportiona l | NA
| TL_VL002 | Swagelok SS31RS4 (Modified) | Liquid expansion | 1/4" Swagelok | 100 | 212 | -65 | 343 | NA | 0.012 Nom / 0.04 max | 1.6 | NA | NA | NA | Proportiona l | NA
| TL_VL003 | Swagelok SS-4UW-TW | Test evaporator inlet | 1/4" socket weld | 100 | 172 | -29 | 343 | NA | 0.36 | 4.4 | NA | NA | NA | Proportiona l | NA
| TL_VL004 | Swagelok SS-4UW-TW | Evaporator inlet | 1/4" socket weld | 100 | 172 | -29 | 343 | NA | 0.36 | 4.4 | NA | NA | NA | Proportiona | NA
| TL_VL006 | Swagelok SS-6UW-TW | Test evaporator outlet | 3/8" socket weld | 100 | 172 | -29 | 343 | NA | 1 | 7.1 | NA | NA | NA | Proportiona l | NA
| TL_VL007 | Swagelok SS-58SW8T | Check valve with modified poppet | 1/2" socket weld | 100 | 307 | -53 | 176 | NA | 2.2 | 11. 1 | NA | NA | NA | NA | NA
| TL_VL008 | Swagelok SS-6UW-TW | Transfer tube shut-off | 3/8" socket weld | 100 | 172 | -29 | 343 | NA | 1 | 4.4 | NA | NA | NA | Proportiona l | NA
| TL_VL009 | TBV | Tert. vacuum evacuation | CF16 | 2 | NA | NA | NA | NA | NA | N A | NA | NA | NA | Proportiona l | NA
| TL_VL103 | Swagelok SS- 43GXVCR4-42dcx | 3-way Condenser selection | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 0.9 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
| TLR_VL002 | Swagelok SS-6UW-TW | Left right inter connect | 3/8" socket weld | 100 | 172 | -29 | 343 | NA | 1 | 7.1 | NA | NA | NA | Proportiona l | NA
| TLR_VL107 | Swagelok SS- 43GHLVCR4 | Filling port | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 2.4 | 4.8
| TR_VL001 | Swagelok SS-4UW-TW | Transfer tube shut-off | 1/4" socket weld | 100 | 172 | -29 | 343 | NA | 0.36 | 4.4 | NA | NA | NA | Proportiona l | NA
| TR_VL002 | Swagelok SS31RS4 (Modified) | Liquid expansion | 1/4" Swagelok | 100 | 212 | -65 | 343 | NA | 0.012 Nom / 0.04 max | 1.6 | NA | NA | NA | Proportiona l | NA
| TR_VL003 | Swagelok SS-4UW-TW | Test evaporator inlet | 1/4" socket weld | 100 | 172 | -29 | 343 | NA | 0.36 | 4.4 | NA | NA | NA | Proportiona l | NA
| TR_VL004 | Swagelok SS-4UW-TW | Evaporator inlet | 1/4" socket weld | 100 | 172 | -29 | 343 | NA | 0.36 | 4.4 | NA | NA | NA | Proportiona l | NA
| TR_VL006 | Swagelok SS-6UW-TW | Test evaporator outlet | 3/8" socket weld | 100 | 172 | -29 | 343 | NA | 1 | 7.1 | NA | NA | NA | Proportiona l | NA
| TR_VL007 | Swagelok SS-58SW8T | Check valve with modified poppet | 1/2" socket weld | 100 | 307 | -53 | 176 | NA | 2.2 | 11. 1 | NA | NA | NA | NA | NA
| TR_VL008 | Swagelok SS-6UW-TW | Transfer tube shut-off | 1/4" socket weld | 100 | 172 | -29 | 343 | NA | 1 | 4.4 | NA | NA | NA | Proportiona l | NA
| TR_VL009 | TBV | Tert. vacuum evacuation | CF16 | 2 | NA | NA | NA | NA | NA | N A | NA | NA | NA | Proportiona l | NA
| TR_VL103 | Swagelok SS- 43GXVCR4-42dcx | 3-way Condenser selection | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 0.9 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch
| TR_VL108 | Swagelok SS- 43GXVCR4-42dcx | Pump shut- off/TLR pump cooling | 1/4"VCR male | 100 | 172 | -53 | 37 | NA | 0.9 | 4.8 | 24Vdc | 22 | motor/end switch |  | Position switch

## EH
New code | Code | Part | Function | Supply (V) | Column1 | Power (W) | Resistance (Ohm) | Electrical control | Output signal | Diamater (mm) | Length (mm) | No-heat length (mm) | Heated area (cm2) | Thermocouple location | Heat flux (W/cm2) | Column2
| TL_HT001 | 2 parallel / 3 serial Watlow K010030c500000 | Module base temperature control | 30 | DC | 34.8 | 52.3Ω/3*2 = 8.7Ω | DC Voltage regulation |  |  |  |  | 19.4 |  | 1.8
| TL_HT002 | 2 parallel / 3 serial Watlow K010030c500000 | Module base temperature control | 30 | DC | 34.8 | 52.3Ω/3*2 = 8.7Ω | DC Voltage regulation |  |  |  |  | 19.4 |  | 1.8
| TL_HT003 | 2 parallel / 3 serial Watlow K010030c500000 | Module base temperature control | 30 | DC | 34.8 | 52.3Ω/3*2 = 8.7Ω | DC Voltage regulation |  |  |  |  | 19.4 |  | 1.8
| TL_HT004 | 2 parallel / 3 serial Watlow K010030c500000 | Module base temperature control | 30 | DC | 34.8 | 52.3Ω/3*2 = 8.7Ω | DC Voltage regulation |  |  |  |  | 19.4 |  | 1.8
EH1a02 | TL_HT102 | Watlow: Silicon Heater pads | Pump oil heater | 240 | AC | 130 | 443.1 | PWM |  |  |  |  | 130.0 |  | 1.0
EH1a04 | TL_HT103 | Watlow: KFRJ016DM003A | Liquid line damper | 220 | AC | 50 | 968 | PWM | Internal Thermocouple K | 12.7 | 410 | 350 | 23.9 | center | 2.1 | KFRJ016DM003A Firerod cartridge heater with pins and T/C in the center Diameter: 1/2 " -0.002" -0.006" Length: 410.00 mm (16 9/64") +/-8,20 mm no heat zone at lead end: 350.00 mm (13 25/32'') 220 V, 50 W Watt density: 2.29 W/cm² 250 mm fiberglass insulated leads pin length : 16.00, 16.00 mm T/C K (NiCr-Ni), DIN colour code cavity, potted with epoxy resin
EH1a24 | TL_HT104 | Watlow: KMFG1000M001A | By pass heater | 220 | AC | 2000 | 24.2 | PWM | Internal Thermocouple K | 10 | 1000 | 100 | 282.7 | center | 7.1 | KMFG1000M001A Metric Firerod cartridge heater with pins and T/C in the center Diameter: 10 mm -0,02 mm -0,08 mm Length: 1000.00 mm (39 3/8") +/-20 mm no heat zone at lead end: 100.00 mm (3 15/16'') 220 V, 2000 W Watt density: 7.11 W/cm² 3000 mm fiberglass insulated leads pin length : 8, 8 mm T/C K (NiCr-Ni), ANSI colour code cavity, potted with epoxy resin
EH4a54 | TL_HT105 | Watlow: KFRJ015AM001A | Accumulator heater | 220 | AC | 1000 | 48.4 | PWM | Internal Thermocouple K | 12.7 | 380 | 85 | 117.7 | center | 8.5 | KFRJ015AM001A Firerod cartridge heater with pins and T/C in the center Diameter: 1/2 " -0.002" -0.006" Length: 381.00 mm (15") +/-7,62 mm no heat zone at lead end: 85.00 mm (3 11/32'') 220 V, 1000 W Watt density: 8.62 W/cm² 3000 mm fiberglass insulated leads pin length : 8.00, 8.00 mm T/C K (NiCr-Ni), ANSI colour code cavity, potted with epoxy resin with 35 mm bushing at lead end
| TLR_HT102 | Watlow: TBD | Pump oil heater | 240 | AC | 130 | 443.1 | PWM |  |  |  |  | 130.0 |  | 1.0
| TR_HT001 | 2 parallel / 3 serial Watlow K010030c500000 | Module base temperature control | 30 | DC | 34.8 | 52.3Ω/3*2 = 8.7Ω | DC Voltage regulation |  |  |  |  | 19.4 |  | 1.8
| TR_HT002 | 2 parallel / 3 serial Watlow K010030c500000 | Module base temperature control | 30 | DC | 34.8 | 52.3Ω/3*2 = 8.7Ω | DC Voltage regulation |  |  |  |  | 19.4 |  | 1.8
| TR_HT003 | 2 parallel / 3 serial Watlow K010030c500000 | Module base temperature control | 30 | DC | 34.8 | 52.3Ω/3*2 = 8.7Ω | DC Voltage regulation |  |  |  |  | 19.4 |  | 1.8
| TR_HT004 | 2 parallel / 3 serial Watlow K010030c500000 | Module base temperature control | 30 | DC | 34.8 | 52.3Ω/3*2 = 8.7Ω | DC Voltage regulation |  |  |  |  | 19.4 |  | 1.8
EH1b02 | TR_HT102 | Watlow: TBD | Pump oil heater | 240 | AC | 130 | 443.1 | PWM |  |  |  |  | 130.0 |  | 1.0
EH1b04 | TR_HT103 | Watlow: KFRJ016DM003A | Liquid line damper | 220 | AC | 50 | 968 | PWM | Internal Thermocouple K | 12.7 | 410 | 350 | 23.9 | center | 2.1
EH1b24 | TR_HT104 | Watlow: KMFG1000M001A | By pass heater | 220 | AC | 2000 | 24.2 | PWM | Internal Thermocouple K | 10 | 1000 | 100 | 282.7 | center | 7.1
EH4b54 | TR_HT105 | Watlow: KFRJ015AM001A | Accumulator heater | 220 | AC | 1000 | 48.4 | PWM | Internal Thermocouple K | 12.7 | 380 | 85 | 117.7 | center | 8.5

## LT
New Code | Code | Part number | Function | Connection | Operating Pressure (Bar)
LT4a54 | TL_LT101 | American Magnetics Model 175 RF | TL Accumulator liquid level | 1/2" male NPT | 100
Lt4b54 | TR_LT101 | American Magnetics Model 175 RF | TR Accumulator liquid level | 1/2" male NPT | 100

## Pumps
New | Code | Part | Function | Connection | Pressure head (Bar) | Flow range (ml/s) | Supply (V) | Power (W) | Electrical control | Manual control | Output signal | Remarks
GP5020 |  |  | Gas Compressor
LP1a02 | TL_PM101 | LEWA 475967- 010.001 | Liquid pump | G 3/8 Fem | 99 max | 1 – 18 (4-65 l/h) | 380 VAC 3p 50Hz | 1500 max | on/off | Manual flow control | Membrane leak detection switch
LP1b02 | TR_PM101 | LEWA 475967- 010.001 | Liquid pump | G 3/8 Fem | 99 max | 1 - 18 (4-65 l/h) | 380 VAC 3p 50Hz | 1500 max | on/off | Manual flow control | Membrane leak detection switch
| TLR_PM101 | LEWA 475967- 010.001 | Liquid pump | G 3/8 Fem | 99 max | 1 - 18 (4-65 l/h) | 380 VAC 3p 50Hz | 1500 max | on/off | Manual flow control | Membrane leak detection switch
| SA_PM101 | Bitzer 2CC-3.2Y | Gas Compressor | 7/8" in / 5/8" out | 28 max | 4511 (16.2 m3/h) @ 50Hz | 380 VAC 3p 25-70Hz |  | Frequency regulation
| SB_PM101 | Bitzer 2KC- 05.2y | Gas Compressor | 5/8" in / 1/2" out | 28 max | 1130 (4.06 m3/h @ 50 Hz) | 380 VAC 3p 50Hz |  | on/off |  |  | Integral in condensing aggregate: Bitzer LH32/2KC-05.2y

## AC
New | Code | Part | Function | Connection | Volume | Operating Pressure (Bar) | Maximum design pressure (Bar) | Minimum design temperature (C) | Maximum design temperature (C) | Remarks
AC5004
AC1a04
AC1b04
AC4a54 | TL_AC101 | TVC51 | CO2 pressure control | Multiple | 14 | 74 | 135 | -55 | 30 | Nikhef engineered
AC4b54 | TR_AC101 | TVC51 | CO2 pressure control | Multiple | 14 | 74 | 135 | -55 | 30 | Nikhef engineered
| SA_AC101 | Danfoss UOB 1/040B0010/040B0142 | Oil separator | 1/2" Solder | 0.52 | 28 | 36 | -40 | 120
| SA_AC102 | Bitzer: F56 | Liquid buffering | 3/8" solder | 5.6 | 20 | 33 | -10 | 120
| SB_AC102 | Bitzer: FS36 | Liquid buffering | 3/8" solder | 3 | 20 | 33 | -10 | 120 | Integral in condensing aggregate: Bitzer LH32/2KC-05.2y

## HX
Code 1 | Code 2 | Code | Contra HX | Part | Function | Connection | Operating pressure (Bar) | Maximum design pressure (Bar) | Minimum design temperature (℃) | Maximum design temperature (℃) | Heat exchange area (mm2)
HX5002 | NA
|  | TL_HX001 | PU01_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX002 | PU02_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX003 | VL01_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX004 | VL02_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX005 | VL03_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX006 | VL04_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX007 | VL05_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX008 | VL06_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX009 | VL07_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX010 | VL08_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX011 | VL09_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX012 | VL10_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX013 | VL11_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX014 | VL12_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX015 | VL13_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX016 | VL14_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX017 | VL15_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX018 | VL16_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX021 | VL19_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX024 | VL22_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX025 | VL23_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX026 | VL24_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX027 | VL25_A | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TL_HX028 | TL_HX105 | TVC12 | Vapor transfer line | 1/2" VCR female | 90 | 135 | -50 | 30 | 953568
|  | TL_HX101 | SA_HX103 | TVC72 / SWEPB16DWHx12/1P-SC-H 4x1/2"INT.NPT | Main condenser | 1/2"FNPT | 68 | 135 | -55 | 30 | 164000
HX5a08 | HX9a64 | TL_HX102 | SB_HX103 | TVC72 / SWEPB16DWHx6/1P-SC-H 4x1/2"INT.NPT | Back-up condenser | 1/2"FNPT | 68 | 135 | -55 | 30 | 410000
HX5b08 | HX4a54a | TL_HX103 | SA_HX107 | 3/8"x0.035"x10m SS Tube integral in TVC51 | Main accu vaporator spiral | 1/4HVCR male | -68 | -135 | -55 | 30 | 299080
HX1a10 | HX4a54b | TL_HX104 | SB_HX107 | 3/8"x0.035"x10m SS Tube integral in TVC51 | Back-up accu vaporator spiral | 1/4HVCR male | -68 | -135 | -55 | 30 | 299080
TL | TL | TL_HX106 | TL_HX028 | TVC12 | Liquid transfer line | 1/2" VCR female | 90 | 135 | -50 | 30 | 686569
|  | TR_HX001 | PU01_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX002 | PU02_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX003 | VL01_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX004 | VL02_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX005 | VL03_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX006 | VL04_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX007 | VL05_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX008 | VL06_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX009 | VL07_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX010 | VL08_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX011 | VL09_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX012 | VL10_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX013 | VL11_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX014 | VL12_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX015 | VL13_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX016 | VL14_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX017 | VL15_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX018 | VL16_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX021 | VL19_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX024 | VL22_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX025 | VL23_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX026 | VL24_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX027 | VL25_C | TVD76 | Module cooling | OD4mmx0.7mm weld | 68 | 135 | -40 | 60 | 1436
|  | TR_HX028 | TR_HX105 | TVC12 | Vapor transfer line | 1/2" VCR female | 90 | 135 | -50 | 30 | 931624
|  | TR_HX101 | SA_HX105 | TVC72 / SWEPB16DWHx12/1P-SC-H 4x1/2"INT.NPT | Main condenser | 1/2"FNPT | 68 | 135 | -55 | 30 | 164000
HX5c08 | HX9b64 | TR_HX102 | SB_HX105 | TVC72 / SWEPB16DWHx6/1P-SC-H 4x1/2"INT.NPT | Back-up condenser | 1/2"FNPT | 68 | 135 | -55 | 30 | 410000
HX5d08 | HX4b54a | TR_HX103 | SA_HX108 | 3/8"x0.035"x10m SS Tube integral in TVC51 | Main accu vaporator spiral | 1/4HVCR male | -68 | -135 | -55 | 30 | 299080
HX1b10 | HX4b54b | TR_HX104 | SB_HX108 | 3/8"x0.035"x10m SS Tube integral in TVC51 | Back-up accu vaporator spiral | 1/4HVCR male | -68 | -135 | -55 | 30 | 299080
|  | TR_HX105 | TLR_HX105 | TVC135 / 6x 1.5mm*0.25mm*2m | TLR pump liquid inlet cooling | 1/4HVCR female | 90 | 135 | -55 | 40 | 37699
|  | TR_HX106 | TL_HX028 | TVC12 | Liquid transfer line | 1/2" VCR female | 90 | 135 | -50 | 30 | 670769
|  | TLR_HX105 | TR_HX105 | TVC135 / 6x 1.5mm*0.25mm*2m | TLR pump liquid inlet cooling | orbital welding | 90 | 135 | -50 | 30 | xxx
|  | SA_HX101 | CERN Cold water | SWEP B15Hx14 / 1P-SC-S | SA condenser | Soldering | 23 | 32 | 0 | 120 | 504000
|  | SA_HX102 | SA_HX103 super heater | SWEP B5Hx16 / 1P-SC-S | SA superheater | Soldering | 23 | 32 | -50 | 30 | 168000
|  | SA_HX103 | TL_HX101 | TVC72 / SWEPB16DWHx12/1P-SC-H 4x1/2"INT.NPT | SA main evaporator | 1/2"FNPT | 23 | 32 | -50 | 30 | 164000
|  | SA_HX104 | SA_HX105 super heater | SWEP B5Hx16 / 1P-SC-S | SA superheater | Soldering | 23 | 32 | -50 | 30 | 168000
|  | SA_HX105 | TR_HX101 | TVC72 / SWEPB16DWHx12/1P-SC-H 4x1/2"INT.NPT | SA main evaporator | 1/2"FNPT | 23 | 32 | -50 | 30 | 164000
|  | SA_HX106 | Subcooler | SWEP B5Hx16 / 1P-SC-S | SA sub cooler | Soldering | 23 | 32 | -50 | 30 | 168000
|  | SA_HX107 | TL_HX103 | 3/8"x0.035"x10m SS Tube integral in TVC51 | Main accu vaporator spiral | 1/4HVCR male | -68 | -135 | -55 | 30 | 296881
|  | SA_HX108 | TR_HX103 | 3/8"x0.035"x10m SS Tube integral in TVC51 | Main accu vaporator spiral | 1/4HVCR male | -68 | -135 | -55 | 30 | 296881
|  | SB_HX101 | Ambient air | Bitzer LH32/2KC-05.2Y integral | SB condenser | Soldering | 23 | 32 | -50 | 30 | 249319
|  | SB_HX103 | TL_HX102 | TVC72 / SWEPB16DWHx6/1P-SC-H 4x1/2"INT.NPT | SB main evaporator | 1/2"FNPT | 23 | 32 | -50 | 30 | 410000
|  | SB_HX105 | TR_HX102 | TVC72 / SWEPB16DWHx6/1P-SC-H 4x1/2"INT.NPT | SB main evaporator | 1/2"FNPT | 23 | 32 | -50 | 30 | 410000
|  | SB_HX106 | Subcooler | SWEP B5Hx16 / 1P-SC-S | SB sub cooler | Soldering | 23 | 32 | -50 | 30 | 168000
|  | SB_HX107 | TL_HX104 | 3/8"x0.035"x10m SS Tube integral in TVC51 | Main accu vaporator spiral | 1/4HVCRmale | -68 | -135 | -55 | 30 | 296881
|  | SB_HX108 | TR_HX104 | 3/8"x0.035"x10m SS Tube integral in TVC51 | Main accu vaporator spiral | 1/4HVCRmale | -68 | -135 | -55 | 30 | 296881

## BD
New code | Code | Part number | Functionality | Burst Pressure (Bar)
| TL_BD001 | Swagelok SS-RDK-16-1900 | Local control box liquid line safety | 130+/- 7 bar
| TL_BD002 | SwagelokSS-RDK-16-1900 | Local control box vapor line safety | 130+/- 7 bar
| TL_BD002 | SwagelokSS-RDK-16-1900 | Local control box vapor line safety | 130+/- 7 bar
| TL_BD004 | TBD | Tertiary vacuum safety | 1.5
| TR_BD001 | SwagelokSS-RDK-16-1900 | Local control box liquid line safety | 130+/- 7 bar
| TR_BD002 | SwagelokSS-RDK-16-1900 | Local control box vapor line safety | 130+/- 7 bar
| TR_BD002 | SwagelokSS-RDK-16-1900 | Local control box vapor line safety | 130+/- 7 bar
| TR_BD004 | TBD | Tertiary vacuum safety | 1.5
BD9a58 | TL_BD101 | SwagelokSS-RDK-16-1900 | Vapor line safety | 130+/- 7 bar
BD9a60 | TL_BD102 | SwagelokSS-RDK-16-1900 | Condenser safety | 130+/- 7 bar
BD4a54 | TL_BD103 | SwagelokSS-RDK-16-1900 | Accumulator safety | 130+/- 7 bar
BD9a66 | TL_BD104 | SwagelokSS-RDK-16-1900 | Suction line safety | 130+/- 7 bar
SV1a02 | TL_BD105 | SwagelokSS-4R3A-EP | TL-PM101 safety | 130 bar
BD1a04 | TL_BD106 | SwagelokSS-RDK-16-1900 | Pump outlet safety | 130+/- 7 bar
BD1a10 | TL_BD107 | SwagelokSS-RDK-16-1900 | Liquid line safety | 130+/- 7 bar
BD9b58 | TR_BD101 | SwagelokSS-RDK-16-1900 | Vapor line safety | 130+/- 7 bar
BD9b60 | TR_BD102 | SwagelokSS-RDK-16-1900 | Condenser safety | 130+/- 7 bar
BD4b54 | TR_BD103 | SwagelokSS-RDK-16-1900 | Accumulator safety | 130+/- 7 bar
BD9b66 | TR_BD104 | SwagelokSS-RDK-16-1900 | Suction line safety | 130+/- 7 bar
SV1b02 | TR_BD105 | SwagelokSS-4R3A-EP | TR-PM101 safety | 130 bar
BD1b04 | TR_BD106 | SwagelokSS-RDK-16-1900 | Pump outlet safety | 130+/- 7 bar
BD1b10 | TR_BD107 | SwagelokSS-RDK-16-1900 | Liquid line safety | 130+/- 7 bar
| TLR_BD105 | SwagelokSS-4R3A-EP | TRL-PM101 safety | 130 bar

## FL
New code | Code | Part number | Function | Connection | Operating Pressure (Bar) | Maximum Design Pressure (Bar) | Minimum design temperature (°C) | Maximum design temperature (°C) | Pories (micron)
FL5006
| TL_FL001 | Swagelok SS-4FW-VCR-15 | TL-VL002 protection | 1/4" male VCR | 100 | 413 | -28 | 37 | 15
| TL_FL002 | Swagelok element ss-4f-k4-15 | Evaporator Capillary protection | [5 empty] | 15
| TR_FL001 | Swagelok SS-4FW-VCR-15 | TL-VR002 protection | 1/4" male VCR | 100 | 413 | -28 | 37 | 15
| TR_FL002 | Swagelok element ss-4f-k4-15 | Evaporator Capillary protection |  | 100 | 413 | -28 | 37 | 15
FL9a56 | TL_FL101 | Swagelok ss-4TF-TW-15 | Transfer tube filter | 3/8" Weld | 100 | 413 | -28 | 37 | 15
FL1a20 | TL_FL102 | Swagelok ss-4TF-TW-15 | TL-VL109 protection | 1/4" Weld | 100 | 413 | -28 | 37 | 15
FL9b56 | TR_FL101 | Swagelok ss-4TF-TW-15 | Transfer tube filter | 3/8" Weld | 100 | 413 | -28 | 37 | 15
FL1b20 | TR_FL102 | Swagelok ss-4TF-TW-15 | TL-VR109 protection | 1/4" Weld | 100 | 413 | -28 | 37 | 15
| TR_FL103 | Swagelok SS-4FW-VCR-15 | TLR pump culling capillary protection | 1/4" male VCR | 100 | 413 | -28 | 37 | 15
| SA_FL101 | Danfoss DML 033s/023Z5050 | Liquid line filtering | 3/8 solder
| SB_FL101 | Danfoss DML032s/023Z5048 | Liquid line filtering | 1/4 solder

## Alarms
Category | Type | Cause | PLC label | PVSS label | General actions / Failure category | Procedign | Triggered by | Timer involved | Timer setting PVSS label | Timer value | Running timer | Running timer PVSS label | Threshold PLC variable | Threshold PVSS label | Threshold value
Heater | Alarm | Tx Clixon alarm | Clixon_alarm | Tx_HA101--- Clixon_alarm | Heater relais off | continue procedures | Clixon_stat us | [7 empty] | 1
| Alarm | TL Bridge heater too hot | bridge_htr2_t oo_hot_TL | TL_HA030--- bridge_htr2_to o_hot | Bridge heater relais off | continue procedures | TL_TT045, smoke sniffer | [5 empty] | BridgeHeater_max | Tx_HL030--- BridgeHeater_ max | 40
| Alarm | TL pump oil too cold | TL_HT102_t oo_cold | TL_HA101--- HT102_too_col d | TL pump failure | restart | TL_TT122 | [5 empty] | TL_R_LR_HT102_ MIN | Tx_HL101--- R_LR_HT102_ MIN | 10
| Alarm | TL pump oil too hot | TL_HT102_t oo_hot | TL_HA102--- HT102_too_ho t | Heater relais off | continue procedures | TL_TT122 | [5 empty] | TL_HT102_MAX | TL_HL102--- HT102_MAX | 50
| Alarm | TL damper heater too hot | TL_HT103_t oo_hot | TL_HA103--- HT103_too_ho t | Heater relais off | continue procedures | TL_TT123 | [5 empty] | TL_HT103_MAX | TL_HL103--- HT103_MAX | 160
| Alarm | TL by-pass heater too hot | TL_HT104_t oo_hot | TL_HA104--- HT104_too_ho t | Heater relais off, SA-failure | restart | TL_TT124 | [5 empty] | TL_HT104_MAX | TL_HL104--- HT104_MAX | 120
| Alarm | TL accu heater too hot | TL_HT105_t oo_hot | TL_HA105--- HT105_too_ho t | Heater relais off | continue procedures | TL_TT125 | [5 empty] | TL_HT105_MAX | TL_HL105--- HT105_MAX | 160
| Alarm | TL_HT102 thermocouple error | TL_TT122_er ror | TL_HA112--- TT122_error | Heater relais off | continue procedures | TL_TT122_ error | [7 empty] | 1
| Alarm | TL_HT103 thermocouple error | TL_TT123_er ror | TL_HA113--- TT123_error | Heater relais off | continue procedures | TL_TT123_ error | [7 empty] | 1
| Alarm | TL_HT104 thermocouple error | TL_TT124_er ror | TL_HA114--- TT124_error | Heater relais off | continue procedures | TL_TT124_ error | [7 empty] | 1
| Alarm | TL_HT105 thermocouple error | TL_TT125_er ror | TL_HA115--- TT125_error | Heater relais off | continue procedures | TL_TT125_ error | [7 empty] | 1
| Warning | TL pump oil too warm | TL_HT102_h ot_warning | TL_HW102--- HT102_hot_wa rning | Switch off TL_HT102 | continue procedures | TL_TT122 | [5 empty] | TL_HT102_MAX_ WARN | TL_HL106--- HT102_MAX_ WARN | 40
| Warning | TL damper heater too warm | TL_HT103_h ot_warning | TL_HW103--- HT103_hot_wa rning | Switch off TL_HT103 | continue procedures | TL_TT123 | [5 empty] | TL_HT103_MAX_ WARN | TL_HL107--- HT103_MAX_ WARN | 120
|  | TL by-pass heater | TL_HT104_h | TL_HW104--- HT104_hot_wa | Switch off TL_HT104, | [7 empty] | TL_HT104_MAX_ | TL_HL108--- HT104_MAX_
| Warning | too warm | ot_warning | rning | SA-failure | restart | TL_TT124 | [5 empty] | WARN | WARN | 80
| Warning | TL accu heater too warm | TL_HT105_h ot_warning | TL_HW105--- HT105_hot_wa rning | Switch off TL_HT105 | continue procedures | TL_TT125 | [5 empty] | TL_HT105_MAX_ WARN | TL_HL109--- HT105_MAX_ WARN | 120
| Alarm | TL Bridge heater too hot | bridge_htr1_t oo_hot_TR | TR_HA030--- bridge_htr1_to o_hot | Bridge heater relais off | continue procedures | TR_TT045, smoke sniffer | [5 empty] | BridgeHeater_max | Tx_HL030--- BridgeHeater_ max | 40
| Alarm | TR pump oil too cold | TR_HT102_t oo_cold | TR_HA101--- HT102_too_col d | TR pump failure | restart | TR_TT122 | [5 empty] | TR_R_LR_HT102_ MIN | Tx_HL101--- R_LR_HT102_ MIN | 10
| Alarm | TR pump oil too hot | TR_HT102_t oo_hot | TR_HA102--- HT102_too_ho t | Heater relais off | continue procedures | TR_TT122 | [5 empty] | TR_HT102_MAX | TR_HL102--- HT102_MAX | 50
| Alarm | TR damper heater too hot | TR_HT103_t oo_hot | TR_HA103--- HT103_too_ho t | Heater relais off | continue procedures | TR_TT123 | [5 empty] | TR_HT103_MAX | TR_HL103--- HT103_MAX | 160
| Alarm | TR by-pass heater too hot | TR_HT104_t oo_hot | TR_HA104--- HT104_too_ho t | Heater relais off, SA-failure | restart | TR_TT124 | [5 empty] | TR_HT104_MAX | TR_HL104--- HT104_MAX | 120
| Alarm | TR accu heater too hot | TR_HT105_t oo_hot | TR_HA105--- HT105_too_ho t | Heater relais off | continue procedures | TR_TT125 | [5 empty] | TR_HT105_MAX | TR_HL105--- HT105_MAX | 160
| Alarm | TR_HT102 thermocouple error | TR_TT122_e rror | TR_HA112--- TT122_error | Heater relais off | continue procedures | TR_TT122_ error | [7 empty] | 1
| Alarm | TR_HT103 thermocouple error | TR_TT123_e rror | TR_HA113--- TT123_error | Heater relais off | continue procedures | TR_TT123_ error | [7 empty] | 1
| Alarm | TR_HT104 thermocouple error | TR_TT124_e rror | TR_HA114--- TT124_error | Heater relais off | continue procedures | TR_TT124_ error | [7 empty] | 1
| Alarm | TR_HT105 thermocouple error | TR_TT125_e rror | TR_HA115--- TT125_error | Heater relais off | continue procedures | TR_TT125_ error | [7 empty] | 1
| Warning | TR pump oil too warm | TR_HT102_h ot_warning | TR_HW102--- HT102_hot_wa rning | Switch off TR_HT102 | continue procedures | TR_TT122 | [5 empty] | TR_HT102_MAX_ WARN | TR_HL106--- HT102_MAX_ WARN | 40
| Warning | TR damper heater too warm | TR_HT103_h ot_warning | TR_HW103--- HT103_hot_wa rning | Switch off TR_HT103 | continue procedures | TR_TT123 | [5 empty] | TR_HT103_MAX_ WARN | TR_HL107--- HT103_MAX_ WARN | 120
| Warning | TR by-pass heater too warm | TR_HT104_h ot_warning | TR_HW104--- HT104_hot_wa rning | Switch off TR_HT104, SA-failure | restart | TR_TT124 | [5 empty] | TR_HT104_MAX_ WARN | TR_HL108--- HT104_MAX_ WARN | 80
| Warning | TR accu heater too warm | TR_HT105_h ot_warning | TR_HW105--- HT105_hot_wa rning | Switch off TR_HT105 | continue procedures | TR_TT125 | [5 empty] | TR_HT105_MAX_ WARN | TR_HL109--- HT105_MAX_ WARN | 120
| Alarm | TLR pump oil too cold | TLR_HT102_ too_cold | TLR_HA101--- HT102_too_col d | TLR pump failure | restart | TLR_TT122 | [5 empty] | TL_R_LR_HT102_ MIN | Tx_HL101--- R_LR_HT102_ MIN | 10
| Alarm | TLR pump oil too hot | TLR_HT102_ too_hot | TLR_HA102--- HT102_too_ho t | Heater relais off | continue procedures | TLR_TT122 | [5 empty] | TLR_HT102_MAX | TLR_HL102--- HT102_MAX | 50
| Alarm | TLR_HT102 thermocouple error | TLR_TT122_ error | TLR_HA112--- TT122_error | Heater relais off | continue procedures | TLR_TT122 _error | [7 empty] | 1
| Warning | TLR pump oil too warm | TLR_HT102_ hot_warning | TLR_HW102--- HT102_hot_wa rning | Switch off TLR_HT102 | continue procedures | TLR_TT122 | [5 empty] | TLR_HT102_MAX_ WARN | TLR_HL106--- HT102_MAX_ WARN | 40
Pressure | Alarm | TL Pump head pressure too high | TL_PT104_T OO_HIGH | TL_PA101--- PT104_TOO_ HIGH | TL pump failure | restart | TL_PT104 | [5 empty] | TL_PT104_MAX | TL_PL101--- PT104_MAX | 85
| Alarm | TL Pump dP too high | TL_PT104_101_TOO_HI GH | TL_PA102--- PT104_101_T OO_HIGH | TL pump failure | restart | TL_PT104 - TL_PT101 | WAIT_DISABLE_HIGHP_VL103 | Tx_SC102--- WAIT_DISABLE_HIGHP_VL103 | 20 sec | TL_sw_vl103_ dis_high_p | TL_PC102--- sw_vl103_dis _high_p | TL_PT104_101_MAXDIFF | TL_PL102--- PT104_101_MAXDIFF | 25
| Alarm | TL Pump dP too low | TL_PT104_1 01_TOO_LO W | TL_PA103--- PT104_101_T OO_LOW | TL pump failure | restart | TL_PT104 - TL_PT101 | TL_MAX_STARTTIME | TL_SC103--- TL_MAX_STARTTIME | 5 min | TL_PM101_st arttimer | TL_PC103--- PM101_startt imer | TL_PT104_101_MI NDIFF | TL_PL103--- PT104_101_M INDIFF | 2
[8 empty] | WAIT_DISABLE_LOWP | Tx_SC104--- WAIT_DISABLE_LOWP | 1 min | TL_sw_trans_ dis_low_p | TL_PC104--- sw_trans_dis _low_p
[8 empty] | WAIT_DP_ALARM | Tx_SC105--- WAIT_DP_ALARM | 10 sec | TL_pump_wait _timer | TL_PC105--- pump_wait_ti mer
| Alarm | TL Membrane alarm | TL_PM101_ membr_alar m | TL_PA106--- PM101_membr _alarm | TL pump failure | restart | TL_PT103_ stat_membr | [7 empty] | 1
| Alarm | TL Accu pressure too high | TL_ACCU_P RES_TOO_H IGH | TL_PA107--- ACCU_PRES_ TOO_HIGH | Switch off TL_HT105 | continue procedures | TL_PT102 | [5 empty] | TL_PT102_max | TL_PL107--- PT102_max | 68
| Alarm | TL any PT too high (closed volumes) | TL_ANY_PT _TOO_HIGH | TL_PA108--- ANY_PT_TOO _HIGH | open all internal TL valves | reset procedures | TL_PT101, TL_PT102, TL_PT104 | [5 empty] | MAX_PRESS_CLO SED_VOLUME | TL_PL108--- MAX_PRESS_ CLOSED_VOL UME | 99
| Alarm | TR Pump head pressure too high | TR_PT104_T OO_HIGH | TR_PA101--- PT104_TOO_ HIGH | TR pump failure | restart | TR_PT104 | [5 empty] | TR_PT104_MAX | TR_PL101--- PT104_MAX | 85
| Alarm | TR Pump dP too high | TR_PT104_1 01_TOO_HI GH | TR_PA102--- PT104_101_T OO_HIGH | TR pump failure | restart | TR_PT104 - TR_PT101 | WAIT_DISA BLE_HIGHP _VL103 | Tx_SC102--- WAIT_DISAB LE_HIGHP_V L103 | 20 sec | TR_sw_vl103_ dis_high_p | TR_PC102--- sw_vl103_dis _high_p | TR_PT104_101_M AXDIFF | TR_PL102--- PT104_101_M AXDIFF | 25
| Alarm | TR Pump dP too low | TR_PT104_1 01_TOO_LO W | TR_PA103--- PT104_101_T OO_LOW | TR pump failure | restart | TR_PT104 - TR_PT101 | TR_MAX_S TARTTIME | TR_SC103--- TR_MAX_ST ARTTIME | 5 min | TR_PM101_st arttimer | TR_PC103--- PM101_startt imer | TR_PT104_101_MI NDIFF | TR_PL103--- PT104_101_M INDIFF | 2
[8 empty] | WAIT_DISA BLE_LOWP | Tx_SC104--- WAIT_DISAB LE_LOWP | 1 min | TR_sw_trans_ dis_low_p | TR_PC104--- sw_trans_dis _low_p
[8 empty] | WAIT_DP_A LARM | Tx_SC105--- WAIT_DP_AL ARM | 10 sec | TR_pump_wai t_timer | TR_PC105--- pump_wait_ti mer
| Alarm | TR Membrane alarm | TR_PM101_ membr_alar m | TR_PA106--- PM101_membr _alarm | TR pump failure | restart | TR_PT103_ stat_membr | [7 empty] | 1
| Alarm | TR Accu pressure too high | TR_ACCU_P RES_TOO_H IGH | TR_PA107--- ACCU_PRES_ TOO_HIGH | Switch off TR_HT105 | continue procedures | TR_PT102 | [5 empty] | TR_PT102_max | TR_PL107--- PT102_max | 68
| Alarm | TR any PT too high (closed volumes) | TR_ANY_PT _TOO_HIGH | TR_PA108--- ANY_PT_TOO _HIGH | open all internal TR valves | reset procedures | TL_PT101 or TL_PT102 or TL_PT104 | [5 empty] | MAX_PRESS_CLO SED_VOLUME | TR_PL108--- MAX_PRESS_ CLOSED_VOL UME | 99
| Alarm | TLR Pump head pressure too high | TLR_PT104_ TOO_HIGH | TLR_PA101--- PT104_TOO_ HIGH | TLR pump failure | restart | Tx_PT104 | [5 empty] | TLR_PT104_MAX | TLR_PL101--- PT104_MAX | 85
[13 empty] | P | age 145 o | f 180
| Alarm | TLR Pump dP too high | TLR_PT104_ 101_TOO_HI GH | TLR_PA102--- PT104- 101_TOO_HIG H | TLR pump failure | restart | Tx_PT104 - Tx_PT101 | WAIT_DISA BLE_HIGHP _VL103 | Tx_SC102--- WAIT_DISAB LE_HIGHP_V L103 | 20 sec |  |  | TLR_PT104_101_ MAXDIFF | TLR_PL102--- Tx_PT104_10 1_MAXDIFF | 25
| Alarm | TLR Pump dP too low | TLR_PT104_ 101_TOO_L OW | TLR_PA103--- PT104- 101_TOO_LO W | TLR pump failure | restart | Tx_PT104 - Tx_PT101 | TLR_MAX_ STARTTIME | TLR_SC103-- - TLR_MAX_S TARTTIME | 45 min | TLR_PM101_ starttimer | TLR_PC103- -- PM101_startt imer | TLR_PT104_101_ MINDIFF | TLR_PL103--- Tx_PT104_10 1_MINDIFF | 2
[8 empty] | WAIT_DISA BLE_LOWP | Tx_SC104--- WAIT_DISAB LE_LOWP | 1 min
[8 empty] | WAIT_DP_A LARM | Tx_SC105--- WAIT_DP_AL ARM | 10 sec
| Alarm | TLR Membrane alarm | TLR_PM101 _membr_alar m | TLR_PA106--- PM101_membr _alarm | TLR pump failure | restart | TLR_PT103 _stat_mem br | [7 empty] | 1
| Alarm | SA Discharge pressure too high | SA_PT108_T OO_HIGH | SA_PA101--- SA_PT108_TO O_HIGH | SA-failure | restart | SA_PT108 | [5 empty] | Hardwaresetting |  | 21.5
| Alarm | SA Suction pressure too low | SA_PT108_T OO_LOW | SA_PA102--- SA_PT108_TO O_LOW | SA-failure | restart | SA_PT108 | [5 empty] | Hardwaresetting |  | 0.55
| Alarm | SA liquid in compressor | SA_COMPR _LIQUID_IN | SA_PA103--- SA_COMPR_L IQUID_IN | SA-failure | restart | SA_TT121 - SA_PT107_ TSAT | SA_MAX_S TARTTIME | SA_SC103--- SA_MAX_ST ARTTIME | 5 min | SA_PM101_st arttimer | SA_PC103--- PM101_startt imer
[8 empty] | SA_WAIT_L IQUID_ALA RM | SA_SC104--- SA_WAIT_LI QUID_ALAR M | 30 sec | SA_wait_liquid _alarm | SA_PC104--- wait_liquid_al arm | DIFF_SA_TT121_P T107_TSAT | SL_PL104--- DIFF_SA_TT1 21_PT107_TS AT | 2
| Alarm | SB Discharge pressure too high | SB_PT108_T OO_HIGH | SB_PA101--- SB_PT108_TO O_HIGH | SB-failure | restart | SB_PT108 | [5 empty] | Hardware setting |  | 19.5
| Alarm | SB Suction pressure too low | SB_PT108_T OO_LOW | SB_PA102--- SB_PT108_TO O_LOW | SB-failure | restart | SB_PT108 | [5 empty] | Hardware setting |  | 0.8
| Alarm | SB liquid in compressor | SB_COMPR _LIQUID_IN | SB_PA103--- SB_COMPR_L IQUID_IN | SB-failure | restart | SB_TT121 - SB_PT107_ TSAT | SB_MAX_S TARTTIME | SB_SC103--- SB_MAX_ST ARTTIME | 5 min | SB_PM101_st arttimer | SB_PC103--- PM101_startt imer
[8 empty] | SB_WAIT_L IQUID_ALA RM | SB_SC104--- SB_WAIT_LI QUID_ALAR M | 30 sec | SB_wait_liquid _alarm | SB_PC104--- wait_liquid_al arm | DIFF_SB_TT121_P T103_TSAT | SB_PL104--- DIFF_SB_TT1 21_PT103_TS AT | 2
[13 empty] | DIFF_SB_TT121_P T104_TSAT | SB_PL105--- DIFF_SB_TT1 21_PT104_TS AT | 2
Miscalaneo us | Warning | TL Maxium set point reached | TL_accu_ma x_setpoint | TL_MW101--- accu_max_set point | Saturate set point | continue procedures | TL_PT102 | [5 empty] | TL_max_accu_setp | TL_ML101--- max_accu_set p | 26
| Warning | TL Accu timeout | TL_accu_tim eout_alarm | TL_MW102--- accu_timeout_ alarm | none | continue procedures | TL_PT102 | TIMEOUT_A CCU_HTR | Tx_SC101--- TIMEOUT_A CCU_HTR | 30 min | TL_ACCU_TI MER | TL_MC102--- ACCU_TIME R
| Alarm | TL CO2 frost alarm due to SA | TL_CO2_frost_alarm | TL_MA101--- CO2_frost_alar m | SA-failure | restart | TL_TT112 | [5 empty] | CO2_lowest_temp | Tx_ML101--- CO2 _lowest_te mp | -50
[13 empty] | P | age 146 o | f 180
| Alarm | TL CO2 frost alarm due to SB | TL_CO2_fros t_alarm_SB | TL_MA102--- CO2_frost_alar m_SB | SB-failure | reset procedures | TL_TT112 | SB_WAIT_F ROST_ALA RM | SB_SC102--- SB_WAIT_FR OST_ALARM | 5 min | SB_wait_frost _alarm | TL_MC103--- wait_frost_al arm | CO2_lowest_temp | Tx_ML101--- CO2 _lowest_te mp | -50
| Alarm | TL pump thermal relay | TL_PM101_t herm_relay_ on | TL_MA103--- PM101_therm_ relay_on | TL pump failure | restart | TL_PM101 _Th_rel_sta tus
| Alarm | TL too warm | TL_too_warm_accu | TL_MA104--- too_warm_acc u | SA-failure | restart | TL- PT102_TS AT - TL_target_a ccu_setpoin t | [5 empty] | Too_Warm_Thresh old | Tx_ML104--- Too_Warm_Th reshold | 10
|  |  | TL_too_war m_cookie | TL_MA105--- too_warm_coo kie | Interlock cooling ready | continue procedures | TL_mean_e vaporator - TL_target_a ccu_setpoin t | [5 empty] | Too_Warm_Thresh old | Tx_ML104--- Too_Warm_Th reshold | 10
| Warning | TR Maxium set point reached | TR_accu_ma x_setpoint | TR_MW101--- accu_max_set point | Saturate set point | continue procedures | TR_PT102 | [5 empty] | TR_max_accu_set p | TR_ML101--- max_accu_set p | 26
| Warning | TR Accu timeout | TR_accu_tim eout_alarm1 | TR_MW102--- accu_timeout_ alarm1 | none | continue procedures | TR_PT102 | TIMEOUT_A CCU_HTR | Tx_SC101--- TIMEOUT_A CCU_HTR | 30 min | TR_ACCU_TI MER | TL_MC102--- ACCU_TIME R
| Alarm | TR CO2 frost alarm due to SA | TR_CO2_fros t_alarm | TR_MA101--- CO2_frost_alar m | SA-failure | restart | TR_TT112 | [5 empty] | CO2_lowest_temp | Tx_ML101--- CO2 _lowest_te mp | -50
| Alarm | TR CO2 frost alarm due to SB | TR_CO2_fros t_alarm_SB | TR_MA102--- CO2_frost_alar m_SB | SB-failure | reset procedures | TR_TT112 | SB_WAIT_F ROST_ALA RM | SB_SC102--- SB_WAIT_FR OST_ALARM | 5 min | SB_wait_frost _alarm | TR_MC103-- - wait_frost_al arm | CO2_lowest_temp | Tx_ML101--- CO2 _lowest_te mp | -50
| Alarm | TR pump thermal relay | TR_PM101_t herm_relay_ on | TR_MA103--- PM101_therm_ relay_on | TR pump failure | restart | TR_PM101 _Th_rel_sta tus
| Alarm | TR too warm | TR_too_war m_accu | TR_MA104--- too_warm_acc u | SA-failure | restart | TR- PT102_TS AT - TR_target_ accu_setpoi nt | [5 empty] | Too_Warm_Thresh old | Tx_ML104--- Too_Warm_Th reshold | 10
|  |  | TR_too_war m_cookie | TR_MA105--- too_warm_coo kie | Interlock cooling ready | continue procedures | TR_mean_ evaporator - TR_target_ accu_setpoi nt | [5 empty] | Too_Warm_Thresh old | Tx_ML104--- Too_Warm_Th reshold | 10
| Alarm | TLR pump thermal relay | TLR_PM101 _therm_relay _on | TLR_MA103--- PM101_therm_ relay_on | TLRpump failure | restart | TLR_PM10 1_Th_rel_st atus
| Alarm | SA compressor drive fault | SA_drive_fau lt | SA_MA101--- SA_drive_fault | SA-failure | restart
| Alarm | SA compressor drive alarm | SA_drive_ala rm | SA_MA102--- SA_drive_alar m | SA-failure | restart
| Alarm | SA compresor motor protection | SA_PM101_ motorprotecti on | SA_MA103--- SA_PM101_m otorprotection | SA failure | restart | SA_motor_ protect_ok | [7 empty] | 0
| Alarm | Cooling water too warm | PA_coolingw ater_too_hot | SA_MA104--- PA_coolingwat er_too_hot | SA-failure | restart | PA_TT101 | [5 empty] | PA_TT101_MAX | PA_ML101--- PA_TT101_M AX | 10
| Alarm | SB compresor thermal relay | SB_PM101_t herm_relay_ on | SB_MA103--- SB_PM101_th erm_relay_on | SB failure | reset procedures | SB_PM101 _threlay_no rmope | [7 empty] | 0
[13 empty] | P | age 147 o | f 180
| Alarm | SA power group failure | exd1311_pwr (SA)_alarm | xx_MA101--- exd1311_pwr( SA)_alarm | SA-failure | restart | exd1311_p wrd(SA), exd1311_n otpwrd(SA)
| Alarm | By-pass heater power failure | exd1306_pwr (htr)_alarm | xx_MA102--- exd1306_pwr( htr)_alarm | If used then SA-failure | If used then restart | exd1306_p wrd(heaters ), exd1306_n otpwrd(heat ers), tl_cooldown _power_by pass, tr_cooldown _power_by pass
| Alarm | Diesel group power failure | esd205_pwr( diesel)_alarm | xx_MA103--- esd205_pwr(di esel)_alarm |  | reset procedures | esd205_pw rd(diesel), esd205_not pwrd(diesel ) |  | xx-SC103--- WAIT_POWE R_RETURN |  |  | xx_MC103--- PowerReturn TIimer
| Alarm | CO2 vent alarm | venting_alar m | xx_MA104--- venting_alarm | Global enable off | reset procedures | Vacuum system | [5 empty] | Hardwaresetting |  | 1150 mbar
| Alarm | General Haptas alarm | haptas_alarm | xx_MA105--- haptas_alarm |  | continue procedures
| Alarm | TL Haptas alarm | TL_haptas_e rror_vector | TL_MA105--- haptas_error_v ector |  | continue procedures |  |  |  |  | TL_haptas_tim er | TL_MC105--- haptas_timer
| Alarm | TR Haptas alarm | TR_haptas_e rror_vector | TR_MA105--- haptas_error_v ector |  | continue procedures |  |  |  |  | TR_haptas_ti mer | TR_MC105-- - haptas_timer
| Alarm | TLR Haptas alarm | TLR_haptas_ error_vector | TLR_MA105--- haptas_error_v ector |  | continue procedures |  |  |  |  | TLR_haptas_ti mer | TLR_MC105- -- haptas_timer
Valve | Alarm | TL_VL102 timeout | TL_VL102_al arm | TL_VA102--- VL102_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TL_VL102_tim er | TL_VC102--- VL102_timer
| Alarm | TL_VL103 timeout | TL_VL103_al arm | TL_VA103--- VL103_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_3 WAY_VALV E | Tx_SC107--- TIMEOUT_3 WAY_VALVE | 10 sec | TL_VL103_tim er | TL_VC103--- VL103_timer
| Alarm | TL_VL104 timeout | TL_VL104_al arm | TL_VA104--- VL104_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TL_VL104_tim er | TL_VC104--- VL104_timer
| Alarm | TL_VL109 timeout | TL_VL109_al arm | TL_VA109--- VL109_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TL_VL109_tim er | TL_VC109--- VL109_timer
| Alarm | TL_VL111 timeout | TL_VL111_al arm | TL_VA111--- VL111_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TL_VL111_tim er | TL_VC111--- VL111_timer
| Alarm | TL_VL112 timeout | TL_VL112_al arm | TL_VA112--- VL112_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TL_VL112_tim er | TL_VC112--- VL112_timer
[13 empty] | P | age 148 o | f 180
| Alarm | TR_VL102 timeout | TR_VL102_a larm | TR_VA102--- VL102_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TR_VL102_ti mer | TR_VC102--- VL102_timer
| Alarm | TR_VL103 timeout | TR_VL103_a larm | TR_VA103--- VL103_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_3 WAY_VALV E | Tx_SC107--- TIMEOUT_3 WAY_VALVE | 10 sec | TR_VL103_ti mer | TR_VC103--- VL103_timer
| Alarm | TR_VL104 timeout | TR_VL104_a larm | TR_VA104--- VL104_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TR_VL104_ti mer | TR_VC104--- VL104_timer
| Alarm | TR_VL108 timeout | TR_VL108_a larm | TR_VA108--- VL108_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_3 WAY_VALV E | Tx_SC107--- TIMEOUT_3 WAY_VALVE | 10 sec | TR_VL108_ti mer | TR_VC108--- VL108_timer
| Alarm | TR_VL109 timeout | TR_VL109_a larm | TR_VA109--- VL109_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TR_VL109_ti mer | TR_VC109--- VL109_timer
| Alarm | TR_VL111 timeout | TR_VL111_a larm | TR_VA111--- VL111_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TR_VL111_ti mer | TR_VC111--- VL111_timer
| Alarm | TR_VL112 timeout | TR_VL112_a larm | TR_VA112--- VL112_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TR_VL112_ti mer | TR_VC112--- VL112_timer
| Alarm | TLR_VL101 timeout | TLR_VL101_ alarm | TLR_VA101--- VL101_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TLR_VL101_ti mer | TLR_VC101- -- VL101_timer
| Alarm | TLR_VL109 timeout | TLR_VL109_ alarm | TLR_VA109--- VL109_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_3 WAY_VALV E | Tx_SC107--- TIMEOUT_3 WAY_VALVE | 10 sec | TLR_VL109_ti mer | TLR_VC109- -- VL109_timer
| Alarm | TLR_VL110 timeout | TLR_VL110_ alarm | TLR_VA110--- VL110_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_3 WAY_VALV E | Tx_SC107--- TIMEOUT_3 WAY_VALVE | 10 sec | TLR_VL110_ti mer | TLR_VC110- -- VL110_timer
| Alarm | TLR_VL111 timeout | TLR_VL111_ alarm | TLR_VA111--- VL111_alarm |  | continue, procedure maybe get stucked |  | TIMEOUT_2 WAY_VALV E | Tx_SC106--- TIMEOUT_2 WAY_VALVE | 5 sec | TLR_VL111_ti mer | TLR_VC111- -- VL111_timer
Base plate | Alarm | Base plate freezing alarm | Tx_base_fre ezing | Tx_BA001--- base_freezing | SA-Failure | restart | 2 of TL_TT037, TL_TT038, TL_TT039, TL_TT040 | [5 empty] | BASEPLATE_FREEZING | Tx_BL001--- BASEPLATE_ FREEZING | 0
| Alarm | Base plate too hot | TLbase_too_ hot_TT037 | TL_BA002--- base_too_hot_ TT037 | heater process termination | continue procedures | TL_TT037 | [5 empty] | MAX_TEMP_BASE PLATE | TL_BL002--- MAX_TEMP_B ASEPLATE | 27
|  |  | TLbase_too_hot_TT038 | TL_BA003---base_too_hot_TT038 | heater process termination | continue procedures | TL_TT038 | [5 empty] | MAX_TEMP_BASE PLATE | TL_BL002---MAX_TEMP_BASEPLATE | 27
|  |  | TLbase_too_ hot_TT039 | TL_BA004--- base_too_hot_ TT039 | heater process termination | continue procedures | TL_TT039 | [5 empty] | MAX_TEMP_BASE PLATE | TL_BL002--- MAX_TEMP_B ASEPLATE | 27
|  |  | TLbase_too_ hot_TT040 | TL_BA005--- base_too_hot_ TT040 | heater process termination | continue procedures | TL_TT040 | [5 empty] | MAX_TEMP_BASE PLATE | TL_BL002--- MAX_TEMP_B ASEPLATE | 27
| Alarm | FM455 error per channel | TLbase_TT0 37_error | TL_BA006--- base_TT037_e rror | Switch off TL_HT001 | continue procedures
|  |  | TLbase_TT0 38_error | TL_BA007--- base_TT038_e rror | Switch off TL_HT002
|  |  | TLbase_TT0 39_error | TL_BA008--- base_TT039_e rror | Switch off TL_HT003
|  |  | TLbase_TT0 40_error | TL_BA009--- base_TT040_e rror | Switch off TL_HT004
| Warning | Base plate too cold | TLbase_too_ cold_TT037 | TL_BW002--- base_too_cold _TT037 |  | continue procedures | TL_TT037 | [5 empty] | MIN_TEMP_BASE PLATE | TL_BL003--- MIN_TEMP_B ASEPLATE | 18
|  |  | TLbase_too_ cold_TT038 | TL_BW003--- base_too_cold _TT038 |  |  | TL_TT038 | [5 empty] | MIN_TEMP_BASE PLATE | TL_BL003--- MIN_TEMP_B ASEPLATE | 18
|  |  | TLbase_too_ cold_TT039 | TL_BW004--- base_too_cold _TT039 |  |  | TL_TT039 | [5 empty] | MIN_TEMP_BASE PLATE | TL_BL003--- MIN_TEMP_B ASEPLATE | 18
|  |  | TLbase_too_ cold_TT040 | TL_BW005--- base_too_cold _TT040 |  |  | TL_TT040 | [5 empty] | MIN_TEMP_BASE PLATE | TL_BL003--- MIN_TEMP_B ASEPLATE | 18
| Alarm | Base plate too hot | TRbase_too_ hot_TT037 | TR_BA002--- base_too_hot_ TT037 | heater process termination | continue procedures | TR_TT037 | [5 empty] | MAX_TEMP_BASE PLATE | TR_BL002--- MAX_TEMP_B ASEPLATE | 27
|  |  | TRbase_too_ hot_TT038 | TR_BA003--- base_too_hot_ TT038 | heater process termination | continue procedures | TR_TT038 | [5 empty] | MAX_TEMP_BASE PLATE | TR_BL002--- MAX_TEMP_B ASEPLATE | 27
[13 empty] | P | age 142 o | f 180
|  |  | TRbase_too_ hot_TT039 | TR_BA004--- base_too_hot_ TT039 | heater process termination | continue procedures | TR_TT039 | [5 empty] | MAX_TEMP_BASE PLATE | TR_BL002--- MAX_TEMP_B ASEPLATE | 27
|  |  | TRbase_too_ hot_TT040 | TR_BA005--- base_too_hot_ TT040 | heater process termination | continue procedures | TR_TT040 | [5 empty] | MAX_TEMP_BASE PLATE | TR_BL002--- MAX_TEMP_B ASEPLATE | 27
| Alarm | FM455 error per channel | TRbase_TT0 37_error | TR_BA006--- base_TT037_e rror | Switch off TR_HT001 | continue procedures
|  |  | TRbase_TT0 38_error | TR_BA007--- base_TT038_e rror | Switch off TR_HT002
|  |  | TRbase_TT0 39_error | TR_BA008--- base_TT039_e rror | Switch off TR_HT003
|  |  | TRbase_TT0 40_error | TR_BA009--- base_TT040_e rror | Switch off TR_HT004
| Warning | Base plate too cold | TRbase_too_ cold_TT037 | TR_BW002--- base_too_cold _TT037 |  | continue procedures | TR_TT037 | [5 empty] | MIN_TEMP_BASE PLATE | TR_BL003--- MIN_TEMP_B ASEPLATE | 18
|  |  | TRbase_too_ cold_TT038 | TR_BW003--- base_too_cold _TT038 |  |  | TR_TT038 | [5 empty] | MIN_TEMP_BASE PLATE | TR_BL003--- MIN_TEMP_B ASEPLATE | 18
|  |  | TRbase_too_ cold_TT039 | TR_BW004--- base_too_cold _TT039 |  |  | TR_TT039 | [5 empty] | MIN_TEMP_BASE PLATE | TR_BL003--- MIN_TEMP_B ASEPLATE | 18
|  |  | TRbase_too_ cold_TT040 | TR_BW005--- base_too_cold _TT040 |  |  | TR_TT040 | [5 empty] | MIN_TEMP_BASE PLATE | TR_BL003--- MIN_TEMP_B ASEPLATE | 18
|  | General FM455 alarm | FM455_error | Tx_BA002--- FM455_error

## Old
CO2 Left |  | CO2 Right |  | Transfer valves
VCTS | New | VCTS | New | VCTS | New
TL_PM101 | LP1A02 | TR_PM101 | LP1B02 | TLR_VL110 | EV2002
TL_HT102 | EH1A02 | TR_HT102 | EH1B02 | TLR_VL111 | EV2004
TL_PT103 | PT1A02 | TR_PT103 | PT1B02
TL_VL107 | MV1A02 | TR_VL107 | MV1B02
TL_BD105 | SV1A02 | TR_BD105 | SV1B02
TL_VL108 | MV1A04
TL_HT103 | EH1A04 | TR_HT103 | EH1B04
| AC1A04 |  | AC1B04
TL_FL102 | FL1A20 | TR_FL102 | FL1B20
TL_VL109 | EV1A21 | TR_VL109 | EV1B21
TL_VL110 | AV1A22 | TR_VL110 | AV1B22
TL_HT104 | EH1A24 | TR_HT104 | EH1B24
TL_BD106 | BD1A04 | TR_BD106 | BD1B04
TL_PT104 | PT1A04 | TR_PT104 | PT1B04
TL_VL111 | EV1A06 | TR_VL111 | EV1B06
| EV1A08 |  | EV1B08
TL_VL112 | EV1A10 | TR_VL112 | EV1B10
TL_BD107 | BD1A10 | TR_BD107 | BD1B10
TL_VL113 | MV1A12 | TR_VL113 | MV1B12
TL_FL101 | FL9A06 | TR_FL101 | FL9B06
TL_VL101 | MV9A08 | TR_VL101 | MV9B08
TL_BD101 | BD9A08 | TR_BD101 | BD9B08
TL_VL102 | EV9A10 | TR_VL102 | EV9B10
TL_BD102 | BD9A10 | TR_BD102 | BD9B10
TL_VL104 | EV4A54 | TR_VL104 | EV4B54
TL_VL105 | MV4A54 | TR_VL105 | MV4B54
TL_AC101 | AC4A54 | TR_AC101 | AC4B54
TL_BD103 | BD4A54 | TR_BD103 | BD4B54
TL_LT101 | LT4A54 | TR_LT101 | LT4B54
TL_PT102 | PT4A54 | TR_PT102 | PT4B54
TL_HT105 | EH4A54 | TR_HT105 | EH4B54
TL_HX103 | HX5B08 | TR_HX103 | HX5B08
TL_HX104 | HX1A10 | TR_HX104 | HX1B10
TL_HX102 | HX9A12 | TR_HX102 | HX9B12
TL_VL116 | MV9A12 | TR_VL116 | MV9B12
TL_BD104 | BD9A12 | TR_BD104 | BD9B12
TL_PT101 | PT9A12 | TR_PT101 | PT9B12
TL_VL106 | MV9A14a | TR_VL106 | MV9B14a
TL_VL114 | MV9A14b | TR_VL114 | MV9B14b

## IO-detail
Type | Card | Channel Number | Old | New | Phoenix contact pin number | Electrical patch panel | Pin | Rack patch panel | Pin2 | Comments | Column1 | Total IO:
DI | XDI1 | 0.0 | TL-VL102 open | EV9a60_GH | B0.0 |  | 2 |  | 2
DI | XDI1 | 0.1 | TL-VL102 close | EV9a60_GL | B0.1 |  | 4 |  | 4
DI | XDI1 | 0.2 | TL-VL102move | EV9a60_RUN | B0.2 |  | 9 |  | 9
DI | XDI1 | 0.3 | TL-VL103 prt 2 | EV1a08_GH | B0.3 |  | 2 |  | 2
DI | XDI1 | 0.4 | TL-VL103 close | EV1a08_GM | B0.4 |  | 4 |  | 4
DI | XDI1 | 0.5 | TL-VL103 prt 3 | EV1a08_GL | B0.5 |  | 6 |  | 6
DI | XDI1 | 0.6 | TL-VL103move | EV1a08_RUN | B0.6 |  | 9 |  | 9
DI | XDI1 | 0.7 | TL-VL104 open | EV4a54_GH | B0.7 |  | 2 |  | 2
DI | XDI1 | 1.0 | TL-VL104close | EV4a54_GL | B1.0 |  | 4 |  | 4
DI | XDI1 | 1.1 | TL-VL104 move | EV4a54_RUN | B1.1 |  | 9 |  | 9
DI | XDI1 | 1.2 | TL-VL109 open | EV1a21_GH | B1.2 |  | 2 |  | 2
DI | XDI1 | 1.3 | TL-VL109 close | EV1a21_GL | B1.3 |  | 4 |  | 4
DI | XDI1 | 1.4 | TL-VL109 move | EV1a21_RUN | B1.4 |  | 9 |  | 9
DI | XDI1 | 1.5 | TL-VL111open | EV4b54_GH | B1.5 |  | 2 |  | 2
DI | XDI1 | 1.6 | TL-VL111 close | EV4b54_GL | B1.6 |  | 4 |  | 4
DI | XDI1 | 1.7 | TL-VL111 move | EV4b54_RUN | B1.7 |  | 9 |  | 9
DI | XDI1 | 2.0 | TL-VL112 open | EV1b21_GH | B2.0 |  | 2 |  | 2
DI | XDI1 | 2.1 | TL-VL112 close | EV1b21_GL | B2.1 |  | 4 |  | 4
DI | XDI1 | 2.2 | TL-VL112 move | EV1b21_RUN | B2.2 |  | 9 |  | 9
DI | XDI1 | 2.3 | TR-VL102open | EV9b60_GH | B2.3 |  | 2 |  | 2
DI | XDI1 | 2.4 | TR-VL102 close | EV9b60_GL | B2.4 |  | 4 |  | 4
DI | XDI1 | 2.5 | TR-VL102 move | EV9b60_RUN | B2.5 |  | 9 |  | 9
DI | XDI1 | 2.6 | TR-VL103 prt 2 | EV1b08_GH | B2.6 |  | 2 |  | 2
DI | XDI1 | 2.7 | TR-VL103 close | EV1b08_GM | B2.7 |  | 4 |  | 4
DI | XDI1 | 3.0 | TR-VL103 prt 3 | EV1b08_GL | B3.0 |  | 6 |  | 6
DI | XDI1 | 3.1 | TR-VL103 move | EV1b08_RUN | B3.1 |  | 9 |  | 9
DI | XDI1 | 3.2 | TR-VL104open
DI | XDI1 | 3.3 | TR-VL104 close
DI | XDI1 | 3.4 | TR-VL104 move
DI | XDI1 | 3.5 | TR-VL108 prt 2
DI | XDI1 | 3.6 | TR-VL108 close
DI | XDI1 | 3.7 | TR-VL108 prt 3
DI | XDI2 | 4.0 | TR-VL108move | TSA_OK
DI | XDI2 | 4.1 | TR-VL109 open | TSB_OK
DI | XDI2 | 4.2 | TR-VL109close | LP1a02_TS
DI | XDI2 | 4.3 | TR-VL109 move | LP1b02_TS
DI | XDI2 | 4.4 | TR-VL111 open | PS1a02
DI | XDI2 | 4.5 | TR-VL111 close | PS1b02
DI | XDI2 | 4.6 | TR-VL111 move | GP5020_TS
DI | XDI2 | 4.7 | TR-VL112 open | HX5002_TS
DI | XDI2 | 5.0 | TR-VL112 close
DI | XDI2 | 5.1 | TR-VL112move
DI | XDI2 | 5.2 | TLR-VL101 prt 2
DI | XDI2 | 5.3 | TLR-VL101 close
DI | XDI2 | 5.4 | TLR-VL101 prt 3
DI | XDI2 | 5.5 | TLR-VL101 move
DI | XDI2 | 5.6 | TLR-VL109 prt 2
DI | XDI2 | 5.7 | TLR-VL109 close
DI | XDI2 | 6.0 | TLR-VL109 prt 3
DI | XDI2 | 6.1 | TLR-VL109 move
DI | XDI2 | 6.2 | TLR-VL110 open
DI | XDI2 | 6.3 | TLR-VL110 close
DI | XDI2 | 64 | TLR-VL110 move
DI | XDI2 | 6.5 | TLR-VL111 open
DI | XDI2 | 6.6 | TLR-VL111close
DI | XDI2 | 6.7 | TLR-VL111 move
DI | XDI2 | 7.0 | ESD205 | [6 empty] | Diesel power group
DI | XDI2 | 7.1 | ESD205 | [6 empty] | Diesel power group
DI | XDI2 | 7.2 | EXD1311 | [6 empty] | SA power group
DI | XDI2 | 7.3 | EXD1311 | [6 empty] | SA power group
DI | XDI2 | 7.4 | EXD1306 | [6 empty] | Bypass heater power group
DI | XDI2 | 7.5 | EXD1306 | [6 empty] | Bypass heater power group
DI | XDI2 | 7.6
DI | XDI2 | 7.7
DI | XDI3 | 8.0 | TL-PM101 on | GP5020_CB_OK
DI | XDI3 | 8.1 | TL-PT103 mem | HX5002_CB_OK
DI | XDI3 | 8.2 | TR-PM101 on | 24VDC_5A_CB_OK
DI | XDI3 | 8.3 | TR-PT103 mem | 24VDC_10A_CB_OK
DI | XDI3 | 8.4 | TLR-PM101 on | LP1a02_CB_OK
DI | XDI3 | 8.5 | TLR-PT103 mem | LP1b02_CB_OK
DI | XDI3 | 8.6 | SA-PM101 Status | 24VAC_CB_OK
DI | XDI3 | 8.7 | SA-PT108 L | EHA_CB_OK
DI | XDI3 | 9.0 | SA-PT108 H | EHB_CB_OK
DI | XDI3 | 9.1 | SB-PM101 on | Misc_CB_OK
DI | XDI3 | 9.2 | SB-PT108 L | GP5020_CB_F
DI | XDI3 | 9.3 | SB-PT108 H | HX5002_CB_F
DI | XDI3 | 9.4 | Clixon status | 24VDC_5A_CB_F | [5 empty] | Heater thermal switches
DI | XDI3 | 9.5 | Th C1 status | 24VDC_10A_CB_F | [5 empty] | Left thermal circuit breaker
DI | XDI3 | 9.6 | Th C2 status | LP1a02_CB_F | [5 empty] | Backup thermal circuit breaker
DI | XDI3 | 9.7 | Th C3 status | LP1b02_CB_F | [5 empty] | Right thermal circuit breaker
DI | XDI3 | 10.0 | SB Pm101 th rel. | 24VAC_CB_F
DI | XDI3 | 10.1 | SA Motor Protec | EHA_CB_F
DI | XDI3 | 10.2 | Rack C02 leak | EHB_CB_F | [5 empty] | Floats in bottom of tray?
DI | XDI3 | 10.3 | Rack A-B leak | Misc_CB_F | [5 empty] | Floats in bottom of tray?
DI | XDI3 | 10.4 | Heater status | EHA_ON_DI
DI | XDI3 | 10.5 | I10.5Vac.Stat. | EHB_ON_DI
DI | XDI3 | 10.6 | I 10.6 Vac. Stat. | LP1a02_ON_DI
DI | XDI3 | 10.7 | I 10.7 Vac. Stat | LP1b02_ON_DI
DI | XDI3 | 11.0 | Alow A | GP5020_ON_DI | [5 empty] | ?
DI | XDI3 | 11.1 | Alow C | HX5002_ON_DI | [5 empty] | ?
DI | XDI3 | 11.2 | Smoke | 24VDC_10A_OK | [5 empty] | ?
DI | XDI3 | 11.3 | Chilled | 24VDC_5A_OK
DI | XDI3 | 11.4 | UPSbatt | PS5020_OK
DI | XDI3 | 11.5 | UPS main | PS5020_L
DI | XDI3 | 11.6 |  | CV5e12_OK
DI | XDI3 | 11.7 |  | CV5f14_OK
DO | XDO1 | 0.0 | TL-VL102 open | EV9a60_OPEN_DO |  |  | 1 |  | 1
DO | XDO1 | 0.1 | TL-VL102 close | EV9a60_CLOSE_DO |  |  | 3 |  | 3
DO | XDO1 | 0.2 | TL-VL103 prt 2 | EV1a08_PRT1_DO |  |  | 1 |  | 1
DO | XDO1 | 0.3 | TL-VL103 close | EV1a08_CLOSE_DO |  |  | 3 |  | 3
DO | XDO1 | 0.4 | TL-VL103 prt 3 | EV1a08_PRT2_DO |  |  | 5 |  | 5
DO | XDO1 | 0.5 | TL-VL104 open | EV4a54_OPEN_DO |  |  | 1 |  | 1
DO | XDO1 | 0.6 | TL-VL104 close | EV4a54_CLOSE_DO |  |  | 3 |  | 3
DO | XDO1 | 0.7 | TL-VL109 open | EV1a21_OPEN_DO |  |  | 1 |  | 1
DO | XDO1 | 1.0 | TL-VL109 close | EV1a21_CLOSE_DO |  |  | 3 |  | 3
DO | XDO1 | 1.1 | TL-VL111 open | EV1b21_OPEN_DO |  |  | 1 |  | 1
DO | XDO1 | 1.2 | TL-VL111 close | EV1b21_CLOSE_DO |  |  | 3 |  | 3
DO | XDO1 | 1.3 | TL-VL112 open | EV4b54_OPEN_DO |  |  | 1 |  | 1
DO | XDO1 | 1.4 | TL-VL112 close | EV4b54_CLOSE_DO |  |  | 3 |  | 3
DO | XDO1 | 1.5 | TR-VL102 open | EV9b60_OPEN_DO |  |  | 1 |  | 1
DO | XDO1 | 1.6 | TR-VL102 close | EV9b60_CLOSE_DO |  |  | 3 |  | 3
DO | XDO1 | 1.7 | TR-VL103 prt 2 | EV1b08_PRT1_DO |  |  | 1 |  | 1
DO | XDO2 | 2.0 | TR-VL103 close | EV1b08_CLOSE_DO |  |  | 3 |  | 3
DO | XDO2 | 2.1 | TR-VL103 prt 3 | EV1b08_PRT2_DO |  |  | 5 |  | 5
DO | XDO2 | 2.2 | TR-VL104 open | EHA_ON_DO
DO | XDO2 | 2.3 | TR-VL104 close | EH1a02_DO
DO | XDO2 | 2.4 | TR-VL108 prt 2 | EH1a04_DO
DO | XDO2 | 2.5 | TR-VL108 close | EH1a24_DO
DO | XDO2 | 2.6 | TR-VL108 prt 3 | EH4a54_DO
DO | XDO2 | 2.7 | TR-VL109 open | EHB_ON_DO
DO | XDO2 | 3.0 | TR-VL109 close | EH1b02_DO
DO | XDO2 | 3.1 | TR-VL111 open | EH1b04_DO
DO | XDO2 | 3.2 | TR-VL111 close | EH1b24_DO
DO | XDO2 | 3.3 | TR-VL112 open | EH4b54_DO
DO | XDO2 | 3.4 | TR-VL112 close | LP1a02_ON_DO
DO | XDO2 | 3.5 | Q 3.5 | LP1b02_ON_DO
DO | XDO2 | 3.6 | Q 3.6 | GP5020_ON_DO
DO | XDO2 | 3.7 | Q 3.7 | HX5002_ON_DO
DO | XDO3 | 4.0 | TLR-VL101 prt 2
DO | XDO3 | 4.1 | TLR-VL101 close
DO | XDO3 | 4.2 | TLR-VL101 prt 3
DO | XDO3 | 4.3 | TLR-VL109 prt 2
DO | XDO3 | 4.4 | TLR-VL109 close
DO | XDO3 | 4.5 | TLR-VL109 prt 3
DO | XDO3 | 4.6 | TLR-VL110 open
DO | XDO3 | 4.7 | TLR-VL110 close
DO | XDO3 | 5.0 | TLR-VL111 open
DO | XDO3 | 5.1 | TLR-VL111 close
DO | XDO3 | 5.2 | Q 5.2 Ready A | [6 empty] | ?
DO | XDO3 | 5.3 | Q 5.3 Ready C | [6 empty] | ?
DO | XDO3 | 5.4 | Q 5.4 Vent Inhib. | [6 empty] | Signal from vacuum cabinet
DO | XDO3 | 5.5 | Q 5.5
DO | XDO3 | 5.6 | Q 5.6
DO | XDO3 | 5.7 | Q 5.7
DO | XDO4 | 6.0 | TL-PM101 on
DO | XDO4 | 6.1 | TR-PM101 on
DO | XDO4 | 6.2 | TLR-PM101 on
DO | XDO4 | 6.3 | SB1-PM101on
DO | XDO4 | 6.4 | SB2-Fan on
DO | XDO4 | 6.5 | Heater Power Off
DO | XDO4 | 6.6 | Q 6.6
DO | XDO4 | 6.7 | Q 6.7
DO | XDO4 | 7.0 | Q7.0Br.HTR1 | [6 empty] | Bridge heater 1
DO | XDO4 | 7.1 | Q 7.1 Br. HTR2 | [6 empty] | Bridge heater 2
DO | XDO4 | 7.2 | Q 7.2
DO | XDO4 | 7.3 | Q 7.3
DO | XDO4 | 7.4 | Q 7.4
DO | XDO4 | 7.5 | Q 7.5
DO | XDO4 | 7.6 | Q 7.6
DO | XDO4 | 7.7 | Q 7.7
DO | XDO5 | 8.0 | TL-HT101 | EX5a08_DO | 3 |  |  |  |  | Cabinet SSRs
DO | XDO5 | 8.1 | TL-HT102 | EX5b08_DO | 4 |  |  |  |  | Cabinet SSRs
DO | XDO5 | 8.2 | TL-HT103 | EX5c08_DO | 5 |  |  |  |  | Cabinet SSRs
DO | XDO5 | 8.3 | TL-HT104 | EX5d08_DO | 6 |  |  |  |  | Cabinet SSRs
DO | XDO5 | 8.4 | TL-HT105
DO | XDO5 | 8.5 | TR-HT101
DO | XDO5 | 8.6 | TR-HT102
DO | XDO5 | 8.7 | TR-HT103
DO | XDO5 | 9.0 | TR-HT104
DO | XDO5 | 9.1 | TR-HT105
DO | XDO5 | 9.2 | TLR-HT102
DO | XDO5 | 9.3 | Q 9.3
DO | XDO5 | 9.4 | Q 9.4
DO | XDO5 | 9.5 | Q 9.5
DO | XDO5 | 9.6 | Q 9.6
DO | XDO5 | 9.7 | Q 9.7
DO | XDO5 | 10.0 | SA-VL106
DO | XDO5 | 10.1 | SA-VL110
DO | XDO5 | 10.2 | SA-VL114
DO | XDO5 | 10.3 | SA-VL119
DO | XDO5 | 10.4 | SB-VL106 | [6 empty] | Expansion valves
DO | XDO5 | 10.5 | SB-VL110 | [6 empty] | Expansion valves
DO | XDO5 | 10.6 | SB-VL114 | [6 empty] | Expansion valves
DO | XDO5 | 10.7 | SB-VL119 | [6 empty] | Expansion valves
DO | XDO5 | 11.0 | Q 11.0
DO | XDO5 | 11.1 | Q 11.1
DO | XDO5 | 11.2 | Q 11.2
DO | XDO5 | 11.3 | Q 11.3
DO | XDO5 | 11.4 | Q 11.4
DO | XDO5 | 11.5 | Q 11.5
DO | XDO5 | 11.6 | Q 11.6
DO | XDO5 | 11.7 | Q 11.7
AI | XAI1 | 1 | Curr.TL_HT01 (NOT CONNECTED) | [9 empty] | IO calcs |  | Number |  | AI channels needed
AI | XAI1 | 2 | Curr.TL_HT02 | [11 empty] | Each side | Chiller
AI | XAI1 | 3 | Curr.TL_HT03 | [9 empty] | PT | 4 - 20 | 4 | 2 | 10
AI | XAI1 | 4 | Curr.TL_HT04 | [9 empty] | TT | PT100 | 8 | 5 | 26
AI | XAI1 | 5 | Curr.TR_HT01 (NOT CONNECTED) | [10 empty] | Thermocouple | 0 | 0 | 0
AI | XAI1 | 6 | Curr.TR_HT02 | [13 empty] | 36
AI | XAI1 | 7 | Curr.TR_HT03
AI | XAI1 | 8 | Curr.TR_HT04
AI | XAI1 | 9 | TL_PT001 | [6 empty] | Control (distribution) box pressure sensors
AI | XAI1 | 10 | TL_PT002 | [6 empty] | Control (distribution) box pressure sensors
AI | XAI1 | 11 | TL_PT003 | [6 empty] | Control (distribution) box pressure sensors
AI | XAI1 | 12 | TR_PT001 | [6 empty] | Control (distribution) box pressure sensors
AI | XAI1 | 13 | TR_PT002 | [6 empty] | Control (distribution) box pressure sensors
AI | XAI1 | 14 | TR_PT003 | [6 empty] | Control (distribution) box pressure sensors
AI | XAI1 | 15 | TL_PT101 | PT9a66
AI | XAI1 | 16 | TL_PT102 | PT4a54
AI | XAI2 | 1 | TL_PT104 | PT1a04
AI | XAI2 | 2 | TR_PT101 | PT9b66
AI | XAI2 | 3 | TR_PT102 | PT4b54
AI | XAI2 | 4 | TR_PT104 | PT1b04
AI | XAI2 | 5 | SA_PT101
AI | XAI2 | 6 | SA_PT102
AI | XAI2 | 7 | SA_PT103
AI | XAI2 | 8 | SA_PT104
AI | XAI2 | 9 | SA_PT105
AI | XAI2 | 10 | SA_PT106
AI | XAI2 | 11 | SA_PT107
AI | XAI2 | 12 | SB_PT102
AI | XAI2 | 13 | SB_PT103
AI | XAI2 | 14 | SB_PT104
AI | XAI2 | 15 | SB_PT105
AI | XAI2 | 16 | SB_PT106
AI | XAI3 | 1 | Temp Rack | ??
AI | XAI3 | 2 | Temp Rack | ??
AI | XAI3 | 3 | TL_TT121 | TT1a04a | [5 empty] | Only heater and damper temperatures are directly measured.
AI | XAI3 | 4 | TL_TT122 | TT1a02d | [5 empty] | Thermocouples
AI | XAI3 | 5 | TL_TT123 | TT1a04c
AI | XAI3 | 6 | TL_TT124 | TT1a24
AI | XAI3 | 7 | TL_TT125 | TT4a54d
AI | XAI3 | 8 | TR_TT121 | TT1b04a
AI | XAI3 | 9 | TR_TT122 | TT1b02d
AI | XAI3 | 10 | TR_TT123 | TT1b04c
AI | XAI3 | 11 | TR_TT124 | TT1b24
AI | XAI3 | 12 | TR_TT125 | TT4b54d
AI | XAI3 | 13 | TLR_TT122
AI | XAI3 | 14 | PIW 730 | ?? | [5 empty] | Don't know what this is
AI | XAI3 | 15 | TL_LT101 | LT4a54
AI | XAI3 | 16 | TR_LT101 | LT4b54
AI | XAI4 | 1 | SA_TT109 | [6 empty] | Haptas sensors were used for monitoring freon temperatures in the chiller evaporators and condensors
AI | XAI4 | 2 | SA_TT113
AI | XAI4 | 3 | SA_TT116
AI | XAI4 | 4 | SA_TT118
AI | XAI4 | 5 | PA_TT102
AI | XAI4 | 6 | PB_TT101
AI | XAI4 | 7 | PB_TT102
AI | XAI4 | 8 | SB_TT115
AI | XAI4 | 9 | SB_TT116
AI | XAI4 | 10 | SB_TT117
AI | XAI4 | 11 | SB_TT118
AI | XAI4 | 12 | SB_TT119
AI | XAI4 | 13 | SB_TT020
AI | XAI4 | 14 | PT100 Haptas
AI | XAI4 | 15 | PT100 Haptas
AI | XAI4 | 16 | PT100 Haptas
DI | B11 | 1
DI | B11 | 2
DI | B11 | 3
DI | B11 | 4
DI | B11 | 5
DI | B11 | 6
DI | B11 | 7
DI | B11 | 8
AO | B11 | 1 |  | CV5e12_AO
AO | B11 | 2 |  | CV5f14_AO
AO | B11 | 3
AO | B11 | 4
AO | B11 | 5
AO | B11 | 6
AO | B11 | 7
AO | B11 | 8
AO | B11 | 9
AO | B11 | 10
AO | B11 | 11
AO | B11 | 12
AO | B11 | 13
AO | B11 | 14
AO | B11 | 15
AO | B11 | 16
DI | B12 | 9
DI | B12 | 10
DI | B12 | 11
DI | B12 | 12
DI | B12 | 13
DI | B12 | 14
DI | B12 | 15
DI | B12 | 16
AI | B12 | 1
AI | B12 | 2
AI | B12 | 3
AI | B12 | 4
AI | B12 | 5
AI | B12 | 6
AI | B12 | 7
AI | B12 | 8
AI | B12 | 9
AI | B12 | 10
AI | B12 | 11
AI | B12 | 12
AI | B12 | 13
AI | B12 | 14
AI | B12 | 15
AI | B12 | 16

## IO-old
Type | Card | Number | Old | New | Comments | Column1 | Total IO:
DI | B1 | 0.0 | TL-VL102 open | EV9a60_GH | Position indicator | 1(24),2(di) | DI | 112 | xd1 | 1 | 2
DI | B1 | 0.1 | TL-VL102 close | EV9a60_GL | Position indicator |  | DO | 96 |  | 3 | 4
DI | B1 | 0.2 | TL-VL102move | EV9a60_RUN | In motion |  | AI | 80 |  | 5 | 6
DI | B1 | 0.3 | TL-VL103 prt 2 | EV1a08_GH | Connect EV1a08 here because it is three way |  | AO | 16 |  | 7 | 8
DI | B1 | 0.4 | TL-VL103 close | EV1a08_GM | [5 empty] | 9 | 10
DI | B1 | 0.5 | TL-VL103 prt 3 | EV1a08_GL | [5 empty] | 11 | 12
DI | B1 | 0.6 | TL-VL103move | EV1a08_RUN | [5 empty] | 13 | 14
DI | B1 | 0.7 | TL-VL104 open | EV4a54_GH | [5 empty] | 15 | 16
DI | B1 | 1.0 | TL-VL104close | EV4a54_GL | [5 empty] | 17 | 18
DI | B1 | 1.1 | TL-VL104 move | EV4a54_RUN | [5 empty] | 17 | 18
DI | B1 | 1.2 | TL-VL109 open | EV1a21_GH | [5 empty] | 1 | 1
DI | B1 | 1.3 | TL-VL109 close | EV1a21_GL | [5 empty] | 21 | 22
DI | B1 | 1.4 | TL-VL109 move | EV1a21_RUN | [5 empty] | 23 | 24
DI | B1 | 1.5 | TL-VL111open | EV4b54_GH | Connected to TL_VL103 |  |  |  |  | 25 | 26
DI | B1 | 1.6 | TL-VL111 close | EV4b54_GL
DI | B1 | 1.7 | TL-VL111 move | EV4b54_RUN
DI | B1 | 2.0 | TL-VL112 open | EV1b21_GH
DI | B1 | 2.1 | TL-VL112 close | EV1b21_GL
DI | B1 | 2.2 | TL-VL112 move | EV1b21_RUN
DI | B1 | 2.3 | TR-VL102open | EV9b60_GH
DI | B1 | 2.4 | TR-VL102 close | EV9b60_GL
DI | B1 | 2.5 | TR-VL102 move | EV9b60_RUN
DI | B1 | 2.6 | TR-VL103 prt 2 | EV1b08_GH
DI | B1 | 2.7 | TR-VL103 close | EV1b08_GM
DI | B1 | 3.0 | TR-VL103 prt 3 | EV1b08_GL
DI | B1 | 3.1 | TR-VL103 move | EV1b08_RUN
DI | B1 | 3.2 | TR-VL104open
DI | B1 | 3.3 | TR-VL104 close
DI | B1 | 3.4 | TR-VL104 move
DI | B1 | 3.5 | TR-VL108 prt 2
DI | B1 | 3.6 | TR-VL108 close
DI | B1 | 3.7 | TR-VL108 prt 3
DI | B2 | 4.0 | TR-VL108move | TSA_OK
DI | B2 | 4.1 | TR-VL109 open | TSB_OK
DI | B2 | 4.2 | TR-VL109close | LP1a02_TS
DI | B2 | 4.3 | TR-VL109 move | LP1b02_TS
DI | B2 | 4.4 | TR-VL111 open | PS1a02
DI | B2 | 4.5 | TR-VL111 close | PS1b02
DI | B2 | 4.6 | TR-VL111 move | GP5020_TS
DI | B2 | 4.7 | TR-VL112 open | HX5002_TS
DI | B2 | 5.0 | TR-VL112 close
DI | B2 | 5.1 | TR-VL112move
DI | B2 | 5.2 | TLR-VL101 prt 2
DI | B2 | 5.3 | TLR-VL101 close
DI | B2 | 5.4 | TLR-VL101 prt 3
DI | B2 | 5.5 | TLR-VL101 move
DI | B2 | 5.6 | TLR-VL109 prt 2
DI | B2 | 5.7 | TLR-VL109 close
DI | B2 | 6.0 | TLR-VL109 prt 3
DI | B2 | 6.1 | TLR-VL109 move
DI | B2 | 6.2 | TLR-VL110 open
DI | B2 | 6.3 | TLR-VL110 close
DI | B2 | 64 | TLR-VL110 move
DI | B2 | 6.5 | TLR-VL111 open
DI | B2 | 6.6 | TLR-VL111close
DI | B2 | 6.7 | TLR-VL111 move
DI | B2 | 7.0 | ESD205 |  | Diesel power group
DI | B2 | 7.1 | ESD205 |  | Diesel power group
DI | B2 | 7.2 | EXD1311 |  | SA power group
DI | B2 | 7.3 | EXD1311 |  | SA power group
DI | B2 | 7.4 | EXD1306 |  | Bypass heater power group
DI | B2 | 7.5 | EXD1306 |  | Bypass heater power group
DI | B2 | 7.6
DI | B2 | 7.7
DI | B3 | 8.0 | TL-PM101 on | GP5020_CB_OK
DI | B3 | 8.1 | TL-PT103 mem | HX5002_CB_OK
DI | B3 | 8.2 | TR-PM101 on | 24VDC_5A_CB_OK
DI | B3 | 8.3 | TR-PT103 mem | 24VDC_10A_CB_OK
DI | B3 | 8.4 | TLR-PM101 on | LP1a02_CB_OK
DI | B3 | 8.5 | TLR-PT103 mem | LP1b02_CB_OK
DI | B3 | 8.6 | SA-PM101 Status | 24VAC_CB_OK
DI | B3 | 8.7 | SA-PT108 L | EHA_CB_OK
DI | B3 | 9.0 | SA-PT108 H | EHB_CB_OK
DI | B3 | 9.1 | SB-PM101 on | Misc_CB_OK
DI | B3 | 9.2 | SB-PT108 L | GP5020_CB_F
DI | B3 | 9.3 | SB-PT108 H | HX5002_CB_F
DI | B3 | 9.4 | Clixon status | 24VDC_5A_CB_F | Heater thermal switches
DI | B3 | 9.5 | Th C1 status | 24VDC_10A_CB_F | Left thermal circuit breaker
DI | B3 | 9.6 | Th C2 status | LP1a02_CB_F | Backup thermal circuit breaker
DI | B3 | 9.7 | Th C3 status | LP1b02_CB_F | Right thermal circuit breaker
DI | B3 | 10.0 | SB Pm101 th rel. | 24VAC_CB_F
DI | B3 | 10.1 | SA Motor Protec | EHA_CB_F
DI | B3 | 10.2 | Rack C02 leak | EHB_CB_F | Floats in bottom of tray?
DI | B3 | 10.3 | Rack A-B leak | Misc_CB_F | Floats in bottom of tray?
DI | B3 | 10.4 | Heater status | EHA_ON_DI
DI | B3 | 10.5 | I10.5Vac.Stat. | EHB_ON_DI
DI | B3 | 10.6 | I 10.6 Vac. Stat. | LP1a02_ON_DI
DI | B3 | 10.7 | I 10.7 Vac. Stat | LP1b02_ON_DI
DI | B3 | 11.0 | Alow A | GP5020_ON_DI | ?
DI | B3 | 11.1 | Alow C | HX5002_ON_DI | ?
DI | B3 | 11.2 | Smoke | 24VDC_10A_OK | ?
DI | B3 | 11.3 | Chilled | 24VDC_5A_OK
DI | B3 | 11.4 | UPSbatt | PS5020_OK
DI | B3 | 11.5 | UPS main | PS5020_L
DI | B3 | 11.6 |  | CV5e12_OK
DI | B3 | 11.7 |  | CV5f14_OK
DO | B4 | 0.0 | TL-VL102 open | EV9a60_OPEN_DO
DO | B4 | 0.1 | TL-VL102 close | EV9a60_CLOSE_DO
DO | B4 | 0.2 | TL-VL103 prt 2 | EV1a08_PRT1_DO
DO | B4 | 0.3 | TL-VL103 close | EV1a08_CLOSE_DO
DO | B4 | 0.4 | TL-VL103 prt 3 | EV1a08_PRT2_DO
DO | B4 | 0.5 | TL-VL104 open | EV4a54_OPEN_DO
DO | B4 | 0.6 | TL-VL104 close | EV4a54_CLOSE_DO
DO | B4 | 0.7 | TL-VL109 open | EV1a21_OPEN_DO
DO | B4 | 1.0 | TL-VL109 close | EV1a21_CLOSE_DO
DO | B4 | 1.1 | TL-VL111 open | EV1b21_OPEN_DO
DO | B4 | 1.2 | TL-VL111 close | EV1b21_CLOSE_DO
DO | B4 | 1.3 | TL-VL112 open | EV4b54_OPEN_DO
DO | B4 | 1.4 | TL-VL112 close | EV4b54_CLOSE_DO
DO | B4 | 1.5 | TR-VL102 open | EV9b60_OPEN_DO
DO | B4 | 1.6 | TR-VL102 close | EV9b60_CLOSE_DO
DO | B4 | 1.7 | TR-VL103 prt 2 | EV1b08_PRT1_DO
DO | B4 | 2.0 | TR-VL103 close | EV1b08_CLOSE_DO
DO | B4 | 2.1 | TR-VL103 prt 3 | EV1b08_PRT2_DO
DO | B4 | 2.2 | TR-VL104 open | EHA_ON_DO
DO | B4 | 2.3 | TR-VL104 close | EH1a02_DO
DO | B4 | 2.4 | TR-VL108 prt 2 | EH1a04_DO
DO | B4 | 2.5 | TR-VL108 close | EH1a24_DO
DO | B4 | 2.6 | TR-VL108 prt 3 | EH4a54_DO
DO | B4 | 2.7 | TR-VL109 open | EHB_ON_DO
DO | B4 | 3.0 | TR-VL109 close | EH1b02_DO
DO | B4 | 3.1 | TR-VL111 open | EH1b04_DO
DO | B4 | 3.2 | TR-VL111 close | EH1b24_DO
DO | B4 | 3.3 | TR-VL112 open | EH4b54_DO
DO | B4 | 3.4 | TR-VL112 close | LP1a02_DO
DO | B4 | 3.5 | Q 3.5 | LP1b02_DO
DO | B4 | 3.6 | Q 3.6 | GP5020_ON_DO
DO | B4 | 3.7 | Q 3.7 | HX5002_ON_DO
DO | B5 | 4.0 | TLR-VL101 prt 2
DO | B5 | 4.1 | TLR-VL101 close
DO | B5 | 4.2 | TLR-VL101 prt 3
DO | B5 | 4.3 | TLR-VL109 prt 2
DO | B5 | 4.4 | TLR-VL109 close
DO | B5 | 4.5 | TLR-VL109 prt 3
DO | B5 | 4.6 | TLR-VL110 open
DO | B5 | 4.7 | TLR-VL110 close
DO | B5 | 5.0 | TLR-VL111 open
DO | B5 | 5.1 | TLR-VL111 close
DO | B5 | 5.2 | Q 5.2 Ready A |  | ?
DO | B5 | 5.3 | Q 5.3 Ready C |  | ?
DO | B5 | 5.4 | Q 5.4 Vent Inhib. |  | Signal from vacuum cabinet
DO | B5 | 5.5 | Q 5.5
DO | B5 | 5.6 | Q 5.6
DO | B5 | 5.7 | Q 5.7
DO | B5 | 6.0 | TL-PM101 on
DO | B5 | 6.1 | TR-PM101 on
DO | B5 | 6.2 | TLR-PM101 on
DO | B5 | 6.3 | SB1-PM101on
DO | B5 | 64 | SB2-Fan on
DO | B5 | 6.5 | Heater Power Off
DO | B5 | 6.6 | Q 6.6
DO | B5 | 6.7 | Q 6.7
DO | B5 | 7.0 | Q7.0Br.HTR1 |  | Bridge heater 1
DO | B5 | 7.1 | Q 7.1 Br. HTR2 |  | Bridge heater 2
DO | B5 | 7.2 | Q 7.2
DO | B5 | 7.3 | Q 7.3
DO | B5 | 7.4 | Q 7.4
DO | B5 | 7.5 | Q 7.5
DO | B5 | 7.6 | Q 7.6
DO | B5 | 7.7 | Q 7.7
DO | B6 | 8.0 | TL-HT101
DO | B6 | 8.1 | TL-HT102
DO | B6 | 8.2 | TL-HT103
DO | B6 | 8.3 | TL-HT104
DO | B6 | 8.4 | TL-HT105
DO | B6 | 8.5 | TR-HT101
DO | B6 | 8.6 | TR-HT102
DO | B6 | 8.7 | TR-HT103
DO | B6 | 9.0 | TR-HT104
DO | B6 | 9.1 | TR-HT105
DO | B6 | 9.2 | TLR-HT102
DO | B6 | 9.3 | Q 9.3 | EX5a08_DO | Cabinet SSRs
DO | B6 | 9.4 | Q 9.4 | EX5b08_DO | Cabinet SSRs
DO | B6 | 9.5 | Q 9.5 | EX5c08_DO | Cabinet SSRs
DO | B6 | 9.6 | Q 9.6 | EX5d08_DO | Cabinet SSRs
DO | B6 | 9.7 | Q 9.7
DO | B6 | 10.0 | SA-VL106
DO | B6 | 10.1 | SA-VL110
DO | B6 | 10.2 | SA-VL114
DO | B6 | 10.3 | SA-VL119
DO | B6 | 10.4 | SB-VL106 |  | Expansion valves
DO | B6 | 10.5 | SB-VL110 |  | Expansion valves
DO | B6 | 10.6 | SB-VL114 |  | Expansion valves
DO | B6 | 10.7 | SB-VL119 |  | Expansion valves
DO | B6 | 11.0 | Q 11.0
DO | B6 | 11.1 | Q 11.1
DO | B6 | 11.2 | Q 11.2
DO | B6 | 11.3 | Q 11.3
DO | B6 | 11.4 | Q 11.4
DO | B6 | 11.5 | Q 11.5
DO | B6 | 11.6 | Q 11.6
DO | B6 | 11.7 | Q 11.7
AI | B7 | 1 | Curr.TL_HT01 (NOT CONNECTED) | [5 empty] | IO calcs |  | Number |  | AI channels needed
AI | B7 | 2 | Curr.TL_HT02 | [7 empty] | Each side | Chiller
AI | B7 | 3 | Curr.TL_HT03 | [5 empty] | PT | 4 - 20 | 4 | 2 | 10
AI | B7 | 4 | Curr.TL_HT04 | [5 empty] | TT | PT100 | 8 | 5 | 26
AI | B7 | 5 | Curr.TR_HT01 (NOT CONNECTED) | [6 empty] | Thermocouple | 0 | 0 | 0
AI | B7 | 6 | Curr.TR_HT02 | [9 empty] | 36
AI | B7 | 7 | Curr.TR_HT03
AI | B7 | 8 | Curr.TR_HT04
AI | B7 | 9 | TL_PT001 |  | Control (distribution) box pressure sensors
AI | B7 | 10 | TL_PT002 |  | Control (distribution) box pressure sensors
AI | B7 | 11 | TL_PT003 |  | Control (distribution) box pressure sensors
AI | B7 | 12 | TR_PT001 |  | Control (distribution) box pressure sensors
AI | B7 | 13 | TR_PT002 |  | Control (distribution) box pressure sensors
AI | B7 | 14 | TR_PT003 |  | Control (distribution) box pressure sensors
AI | B7 | 15 | TL_PT101 | PT9a66
AI | B7 | 16 | TL_PT102 | PT4a54
AI | B8 | 1 | TL_PT104 | PT1a04
AI | B8 | 2 | TR_PT101 | PT9b66
AI | B8 | 3 | TR_PT102 | PT4b54
AI | B8 | 4 | TR_PT104 | PT1b04
AI | B8 | 5 | SA_PT101
AI | B8 | 6 | SA_PT102
AI | B8 | 7 | SA_PT103
AI | B8 | 8 | SA_PT104
AI | B8 | 9 | SA_PT105
AI | B8 | 10 | SA_PT106
AI | B8 | 11 | SA_PT107
AI | B8 | 12 | SB_PT102
AI | B8 | 13 | SB_PT103
AI | B8 | 14 | SB_PT104
AI | B8 | 15 | SB_PT105
AI | B8 | 16 | SB_PT106
AI | B9 | 1 | Temp Rack | ??
AI | B9 | 2 | Temp Rack | ??
AI | B9 | 3 | TL_TT121 | TT1a04a | Only heater and damper temperatures are directly measured.
AI | B9 | 4 | TL_TT122 | TT1a02d | Thermocouples
AI | B9 | 5 | TL_TT123 | TT1a04c
AI | B9 | 6 | TL_TT124 | TT1a24
AI | B9 | 7 | TL_TT125 | TT4a54d
AI | B9 | 8 | TR_TT121 | TT1b04a
AI | B9 | 9 | TR_TT122 | TT1b02d
AI | B9 | 10 | TR_TT123 | TT1b04c
AI | B9 | 11 | TR_TT124 | TT1b24
AI | B9 | 12 | TR_TT125 | TT4b54d
AI | B9 | 13 | TLR_TT122
AI | B9 | 14 | PIW 730 | ?? | Don't know what this is
AI | B9 | 15 | TL_LT101 | LT4a54
AI | B9 | 16 | TR_LT101 | LT4b54
AI | B10 | 1 | SA_TT109 |  | Haptas sensors were used for monitoring freon temperatures in the chiller evaporators and condensors
AI | B10 | 2 | SA_TT113
AI | B10 | 3 | SA_TT116
AI | B10 | 4 | SA_TT118
AI | B10 | 5 | PA_TT102
AI | B10 | 6 | PB_TT101
AI | B10 | 7 | PB_TT102
AI | B10 | 8 | SB_TT115
AI | B10 | 9 | SB_TT116
AI | B10 | 10 | SB_TT117
AI | B10 | 11 | SB_TT118
AI | B10 | 12 | SB_TT119
AI | B10 | 13 | SB_TT020
AI | B10 | 14 | PT100 Haptas
AI | B10 | 15 | PT100 Haptas
AI | B10 | 16 | PT100 Haptas
DI | B11 | 1
DI | B11 | 2
DI | B11 | 3
DI | B11 | 4
DI | B11 | 5
DI | B11 | 6
DI | B11 | 7
DI | B11 | 8
AO | B11 | 1 |  | CV5e12_AO
AO | B11 | 2 |  | CV5f14_AO
AO | B11 | 3
AO | B11 | 4
AO | B11 | 5
AO | B11 | 6
AO | B11 | 7
AO | B11 | 8
AO | B11 | 9
AO | B11 | 10
AO | B11 | 11
AO | B11 | 12
AO | B11 | 13
AO | B11 | 14
AO | B11 | 15
AO | B11 | 16
DI | B12 | 9
DI | B12 | 10
DI | B12 | 11
DI | B12 | 12
DI | B12 | 13
DI | B12 | 14
DI | B12 | 15
DI | B12 | 16
AI | B12 | 1
AI | B12 | 2
AI | B12 | 3
AI | B12 | 4
AI | B12 | 5
AI | B12 | 6
AI | B12 | 7
AI | B12 | 8
AI | B12 | 9
AI | B12 | 10
AI | B12 | 11
AI | B12 | 12
AI | B12 | 13
AI | B12 | 14
AI | B12 | 15
AI | B12 | 16